## Cover
KSMW-PA2502 - Companion Standard
Data Model
Revision 1.1
2018-09-18
Copyright
Confidential - ©2018 by Honeywell International Inc. All rights reserved. The information in this document is subject to change without notice and does not represent a commitment on the part of Honeywell. The software described in this document is furnished under a license agreement, and may be used or copied only in accordance with the terms of that agreement. No part of this document may be reproduced, transmitted, transcribed, stored in any retrieval system, or translated into any language by any means, electronic or mechanical, including photocopying and recording, for any purpose other than the licensee's personal use without the express written permission of Honeywell. In no event will Honeywell be responsible for any damages, including any lost profits, lost savings or other incidental or consequential damages arising out of the use of this product.
Disclaimer
The information contained in this message (including any attachments) is confidential and intended solely for the attention and use of the named addressee(s). It must not be disclosed to any person without our authority. If you are not the intended recipient, please delete it from your system immediately - any disclosure, copying or distribution thereof or any action taken or omitted to be taken in reliance thereon is prohibited and may be unlawful.

## Revision History
Version | Revisions | Date | Author
0.0 | Initial Draft Version | 2017-11-16 | R. Thor
0.1 | 1st Draft Release | 2017-12-20 | R. Thor
0.2 | Update according: KSMW PA2502 Companion Standard Review List Rev 0.2.xlsx | 2018-01-29 | R. Thor
0.3 | Update according: KSMW PA2502 Companion Standard Review List Rev 0.3.xlsx | 2018-02-22 | R. Thor
0.4 | Update according: KSMW PA2502 Companion Standard Review List Rev 0.4.xlsx | 2018-03-06 | R. Thor
0.5 | Update according: KSMW PA2502 Companion Standard Review List Rev 0.5.xlsx | 2018-03-19 | R. Thor
0.6 | Update according: KSMW PA2502 Companion Standard Review List Rev 0.6.xlsx | 2018-04-06 | R. Thor
1.0 | Update according: KSMW PA2502 Companion Standard Review List Rev 1.0.xlsx | 2018-07-03 | R. Thor
1.1 | Update according: KSMW PA2502 Companion Standard Review List Rev 1.1.xlsx | 2018-09-18 | R. Thor

## Object model
SP PLC | PP PLC | SP GPRS | PP GPRS | # | Object / Attribute Name | Attribute Type | IC |  | OBIS code / Default Value | Access rights [Get, Set, Action], optional if in '( )' | [7 empty] | Comments
PP - 1(6)A - PLC |  | PP - 1(6)A - PLC |  |  | Object / Attribute Name | Attribute Type | Class | Ver. | OBIS code / Default Value | Public (16) | Data Readout (2) | Installation (5) | Maintenance (6) | Certification (7) | FW_update client (3) | PLC Manag. client (4) | Management (1)
x | x | x | x |  | Abstract objects - Association & Security
x | x | x | x |  | SAP Assignment |  | 17 | 0 | 0-0:41.0.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000290000FF" | Get | Get | Get | Get | Get | -- | Get | Get
x | x | x | x | 2 | SAP_assignment_list | asslist_type |  |  | {{1, *}} | Get | Get | Get | Get | Get | -- | Get | Get | One logical device, Server SAP 1
x | x | x | x | 1 | connect_logical_device |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Current association |  | 15 | 3 | 0-0:40.0.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000280000FF" | Get | Get | Get | Get | Get | -- | Get | Get
x | x | x | x | 2 | object_list | object_list_type |  |  |  | Get | Get | Get | Get | Get | -- | Get | Get
x | x | x | x | 3 | associated_partners_id | associated_partners_type |  |  |  | Get | Get | Get | Get | Get | -- | Get | Get
x | x | x | x | 4 | application_context_name | application_context_name |  |  |  | Get | Get | Get | Get | Get | -- | Get | Get
x | x | x | x | 5 | xDLMS_context_info | xDLMS_context_type |  |  |  | Get | Get | Get | Get | Get | -- | Get | Get
x | x | x | x | 6 | authentication_mechanism_name | mechanism_name_structure |  |  |  | Get | Get | Get | Get | Get | -- | Get | Get
x | x | x | x | 7 | secret | octet_string |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | For HLS using GMAC secret is handled via Security setup
x | x | x | x | 8 | association_status | enum |  |  |  | Get | Get | Get | Get | Get | -- | Get | Get
x | x | x | x | 9 | security_setup_reference | octet_string[6] |  |  | "00002B0000FF" | Get | Get | Get | Get | Get | -- | Get | Get
x | x | x | x | 10 | user_list | array (user_list_entry) |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x | 11 | current_user | user_list_entry |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x | 1 | reply_to_HLS_authentication |  |  |  |  | -- | Action | Action | Action | Action | -- | Action | Action
x | x | x | x | 2 | change_HLS_secret |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 3 | add_object |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 4 | remove_object |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 5 | add_user |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x | 6 | remove_user |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x
x | x | x | x |  | Current Security setup |  | 64 | 1 | 0-0:43.0.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00002B0000FF" | -- | Get | Get | Get | Get | -- | Get | Get
x | x | x | x | 2 | security_policy | enum |  |  |  | -- | Get | Get | Get | Get | -- | Get | Get | Bit Security policy 0 unused, shall be set to 0, 1 unused, shall be set to 0, 2 authenticated request, 3 encrypted request, 4 digitally signed request, 5 authenticated response, 6 encrypted response, 7 digitally signed response
x | x | x | x | 3 | security_suite | enum |  |  | 1 | -- | Get | Get | Get | Get | -- | Get | Get | Strengthening the security suite means that the level of protection is increase. Once the protection is increased, it cannot be lowered. allowed range 1 = AES-GCM-128, ECDSA P-256, ECDH P-256, SHA-256, V.44, AES-128 2 = optional until Security suite 2 is available
x | x | x | x | 4 | client_system_title | octet_string[8] |  |  |  | -- | Get | Get | Get | Get | -- | Get | Get
x | x | x | x | 5 | server_system_title | octet_string[8] |  |  |  | -- | Get | Get | Get | Get | -- | Get | Get
x | x | x | x | 6 | certificates | array(certificate_info) |  |  |  | -- | Get | Get | Get | Get | -- | Get | Get | For the server: – Digital Signature Certificate For client: – Digital Signature Certificate 1 – Digital Signature Certificate 2 For Certification Authorities: – Sub-CA 1 (DLMS Server) - Digital Signature Certificate – Sub-CA 2 (DLMS Client) - Digital Signature Certificate – Sub-CA 3 (DLMS Client) - Digital Signature Certificate
x | x | x | x | 1 | security_activate | enum |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | Activates and strengthens the security policy: Strengthening the security policy means that another kind of protection is added. Once a kind of protection is added, it cannot be removed. If the method is invoked with a value indicating a security policy that is weaker than the value of the security_policy attribute, the method invocation fails. The new security policy applies as soon as the method invocation has been confirmed with success. as specified at the security_policy attribute. allowed range: (Bit Security policy) 0 unused, shall be set to 0, 1 unused, shall be set to 0, 2 authenticated request, 3 encrypted request, 4 digitally signed request, 5 authenticated response, 6 encrypted response, 7 digitally signed response
x | x | x | x | 2 | key_transfer | key_transfer |  |  |  | -- | -- | -- | Action | -- | -- | -- | -- | allowed range: (0) global unicast encryption key, (2) authentication key, (3) master key (KEK),
x | x | x | x | 3 | key_argeement | key_agreement |  |  |  | -- | -- | -- | -- | -- | -- |  | Action Req S, Res - | allowed range: (0) global unicast encryption key, (2) authentication key, (3) master key (KEK)
x | x | x | x | 4 | generate_key_pair | enum |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | Generate SERVER key pairs Generates an asymmetric key pair as required by the security suite. The data parameter identifies the usage of the key pair to be generated. Allowed range: (0) digital signature key pair
x | x | x | x | 5 | generate_certificate_request | enum |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | CSR for the SERVER key pairs When this method is invoked, the server sends the Certificate Signing Request (CSR) data that is necessary for a CA to generate a certificate for a server public key. The data parameter identifies the key pair for which the certificate will be requested. allowed range: (0) digital signature key pair,
x | x | x | x | 6 | import_certificate | octet_string |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | Imports an X.509 v3 certificate of a public key. allowed range: For the server: – Digital Signature Certificate For Certification Authorities: – Sub-CA 1 (DLMS Server) - Digital Signature Certificate – Sub-CA 2 (DLMS Client) - Digital Signature Certificate – Sub-CA 3 (DLMS Client) - Digital Signature Certificate
x | x | x | x | 7 | export_certificate | octet_string |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | Exports an X.509 v3 certificate in the server. allowed range: For the server: – Digital Signature Certificate For Certification Authorities: – Sub-CA 1 (DLMS Server) - Digital Signature Certificate – Sub-CA 2 (DLMS Client) - Digital Signature Certificate – Sub-CA 3 (DLMS Client) - Digital Signature Certificate
x | x | x | x | 8 | remove_certificate | octet_string |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | Removes X.509 v3 certificate in the server. allowed range: For Certification Authorities: – Sub-CA 1 (DLMS Server) - Digital Signature Certificate – Sub-CA 2 (DLMS Client) - Digital Signature Certificate – Sub-CA 3 (DLMS Client) - Digital Signature Certificate
x | x | x | x
x | x | x | x |  | Association LN - Management Client |  | 15 | 3 | 0-0:40.0.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000280001FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | object_list | object_list_type |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 3 | associated_partners_id | associated_partners_type |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 4 | application_context_name | application_context_name |  |  | "60857405080103" | -- | -- | -- | Get | -- | -- | -- | Get | Logical_Name_Referencing_With_Ciphering ::= context_id(3)
x | x | x | x | 5 | xDLMS_context_info | xDLMS_context_type |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 6 | authentication_mechanism_name | mechanism_name_structure |  |  | "60857405080207" | -- | -- | -- | Get | -- | -- | -- | Get | HLS mechanism_id 7 (ECDSA)
x | x | x | x | 7 | secret | octet_string |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 8 | association_status | enum |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 9 | security_setup_reference | octet_string[6] |  |  | #VALUE! | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 10 | user_list | array (user_list_entry) |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x | 11 | current_user | user_list_entry |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x | 1 | reply_to_HLS_authentication |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | This method is only applicable to teh 'Current Association' object
x | x | x | x | 2 | change_HLS_secret |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | The new HLS secret is not used with HLS mechanism_id 7 (ECDSA)
x | x | x | x | 3 | add_object |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 4 | remove_object |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 5 | add_user |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x | 6 | remove_user |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x
x | x | x | x |  | Security setup - Management Client |  | 64 | 1 | 0-0:43.0.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00002B0001FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | security_policy | enum |  |  | 0x6C | -- | -- | -- | Get | -- | -- | -- | Get | Bit Security policy 0 unused, shall be set to 0, 1 unused, shall be set to 0, 2 authenticated request, 3 encrypted request, 4 digitally signed request, 5 authenticated response, 6 encrypted response, 7 digitally signed response
x | x | x | x | 3 | security_suite | enum |  |  | 1 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set Req S, Res - | Strengthening the security suite means that the level of protection is increase. Once the protection is increased, it cannot be lowered. allowed range 1 = AES-GCM-128, ECDSA P-256, ECDH P-256, SHA-256, V.44, AES-128 2 = optional until Security suite 2 is available
x | x | x | x | 4 | client_system_title | octet_string[8] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 5 | server_system_title | octet_string[8] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 6 | certificates | array(certificate_info) |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get | For the server: – Digital Signature Certificate For client: – Digital Signature Certificate 1 – Digital Signature Certificate 2 For Certification Authorities: – Sub-CA 2 (DLMS Client) - Digital Signature Certificate
x | x | x | x | 1 | security_activate | enum |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | Activates and strengthens the security policy: Strengthening the security policy means that another kind of protection is added. Once a kind of protection is added, it cannot be removed. If the method is invoked with a value indicating a security policy that is weaker than the value of the security_policy attribute, the method invocation fails. The new security policy applies as soon as the method invocation has been confirmed with success. as specified at the security_policy attribute. allowed range: (Bit Security policy) 0 unused, shall be set to 0, 1 unused, shall be set to 0, 2 authenticated request, 3 encrypted request, 4 digitally signed request, 5 authenticated response, 6 encrypted response, 7 digitally signed response
x | x | x | x | 2 | global_key_transfer | key_data |  |  |  | -- | -- | -- | Action | -- | -- | -- | -- | allowed range: (0) global unicast encryption key, (2) authentication key,
x | x | x | x | 3 | key_argeement | key_agreement |  |  |  | -- | -- | -- | -- | -- | -- | -- | Action Req S, Res - | allowed range: (0) global unicast encryption key, (2) authentication key,
x | x | x | x | 4 | generate_key_pair | enum |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 5 | generate_certificate_request | enum |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 6 | import_certificate | octet_string |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | Imports an X.509 v3 certificate of a public key. allowed range: For client: – Digital Signature Certificate 1 – Digital Signature Certificate 2
x | x | x | x | 7 | export_certificate | octet_string |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | Exports an X.509 v3 certificate in the server. allowed range: For the server: – Digital Signature Certificate For client: – Digital Signature Certificate 1 – Digital Signature Certificate 2 For Certification Authorities: – Sub-CA 2 (DLMS Client) - Digital Signature Certificate
x | x | x | x | 8 | remove_certificate | octet_string |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | Removes X.509 v3 certificate in the server. allowed range: For client: – Digital Signature Certificate 1 – Digital Signature Certificate 2
x | x | x | x
x | x | x | x |  | Rx frame counter - unicast key - Management Client |  | 12544 | 0 | 0-0:43.1.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00002B0101FF" | Get | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 1 | get_frame_counter | octet_string[64] |  |  |  | Action | -- | -- | Action | -- | -- | -- | Action | Method 1: get_frame_counter (data) The challenge is a 64-byte random (octet-string). data ::= challenge challenge Data type: octet-string Authorized value: Decoded as Hexa (Size = 64) Upon invocation of this method, the meter will generate a response to the challenge by performing an HMAC-SHA256(K, m) where K = the AK of the corresponding client and m is the concatenation of Server System Title, Client System Title, received challenge and the frame counter (SysT-S ¦¦ SysT-C ¦¦ Challenge ¦¦ FC) to be returned. data ::= structure { challenge_response: frame_counter: } challenge_response The challenge response value Data type: octet-string Authorized value: Decoded as Hexa (Size = 32) frame_counter: The actual frame counter value Data type: unsigned32 Authorised values: 0x00000000 … 0xFFFFFFFF
x | x | x | x
x | x | x | x |  | Association LN - Data Readout Client |  | 15 | 3 | 0-0:40.0.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000280002FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | object_list | object_list_type |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 3 | associated_partners_id | associated_partners_type |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 4 | application_context_name | application_context_name |  |  | "60857405080103" | -- | -- | -- | Get | -- | -- | -- | Get | Logical_Name_Referencing_With_Ciphering ::= context_id(3)
x | x | x | x | 5 | xDLMS_context_info | xDLMS_context_type |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 6 | authentication_mechanism_name | mechanism_name_structure |  |  | "60857405080207" | -- | -- | -- | Get | -- | -- | -- | Get | HLS mechanism_id 7 (ECDSA)
x | x | x | x | 7 | secret | octet_string |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 8 | association_status | enum |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 9 | security_setup_reference | octet_string[6] |  |  | "00002B0002FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 10 | user_list | array (user_list_entry) |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x | 11 | current_user | user_list_entry |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x | 1 | reply_to_HLS_authentication |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | This method is only applicable to teh 'Current Association' object
x | x | x | x | 2 | change_HLS_secret |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | The new HLS secret is not used with HLS mechanism_id 7 (ECDSA)
x | x | x | x | 3 | add_object |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 4 | remove_object |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 5 | add_user |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x | 6 | remove_user |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x
x | x | x | x |  | Security setup - Data Readout Client |  | 64 | 1 | 0-0:43.0.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00002B0002FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | security_policy | enum |  |  | 0x6C | -- | -- | -- | Get | -- | -- | -- | Get | Bit Security policy 0 unused, shall be set to 0, 1 unused, shall be set to 0, 2 authenticated request, 3 encrypted request, 4 digitally signed request, 5 authenticated response, 6 encrypted response, 7 digitally signed response
x | x | x | x | 3 | security_suite | enum |  |  | 1 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set Req S, Res - | Strengthening the security suite means that the level of protection is increase. Once the protection is increased, it cannot be lowered. allowed range 1 = AES-GCM-128, ECDSA P-256, ECDH P-256, SHA-256, V.44, AES-128 2 = optional until Security suite 2 is available
x | x | x | x | 4 | client_system_title | octet_string[8] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 5 | server_system_title | octet_string[8] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 6 | certificates | array(certificate_info) |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get | For the server: – Digital Signature Certificate For client: – Digital Signature Certificate 1 – Digital Signature Certificate 2 For Certification Authorities: – Sub-CA 2 (DLMS Client) - Digital Signature Certificate
x | x | x | x | 1 | security_activate | enum |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | Activates and strengthens the security policy: Strengthening the security policy means that another kind of protection is added. Once a kind of protection is added, it cannot be removed. If the method is invoked with a value indicating a security policy that is weaker than the value of the security_policy attribute, the method invocation fails. The new security policy applies as soon as the method invocation has been confirmed with success. as specified at the security_policy attribute. allowed range: (Bit Security policy) 0 unused, shall be set to 0, 1 unused, shall be set to 0, 2 authenticated request, 3 encrypted request, 4 digitally signed request, 5 authenticated response, 6 encrypted response, 7 digitally signed response
x | x | x | x | 2 | global_key_transfer | key_data |  |  |  | -- | -- | -- | Action | -- | -- | -- | -- | allowed range: (0) global unicast encryption key, (2) authentication key,
x | x | x | x | 3 | key_argeement | key_agreement |  |  |  | -- | -- | -- | -- | -- | -- | -- | Action Req S, Res - | allowed range: (0) global unicast encryption key, (2) authentication key,
x | x | x | x | 4 | generate_key_pair | enum |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 5 | generate_certificate_request | enum |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 6 | import_certificate | octet_string |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | Imports an X.509 v3 certificate of a public key. allowed range: For client: – Digital Signature Certificate 1 – Digital Signature Certificate 2
x | x | x | x | 7 | export_certificate | octet_string |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | Exports an X.509 v3 certificate in the server. allowed range: For the server: – Digital Signature Certificate For client: – Digital Signature Certificate 1 – Digital Signature Certificate 2 For Certification Authorities: – Sub-CA 2 (DLMS Client) - Digital Signature Certificate
x | x | x | x | 8 | remove_certificate | octet_string |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | Removes X.509 v3 certificate in the server. allowed range: For client: – Digital Signature Certificate 1 – Digital Signature Certificate 2
x | x | x | x
x | x | x | x |  | Rx frame counter - unicast key - Data Readout Client |  | 12544 | 0 | 0-0:43.1.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00002B0102FF" | Get | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 1 | get_frame_counter | octet_string[64] |  |  |  | Action | Action | -- | Action | -- | -- | -- | Action | Method 1: get_frame_counter (data) The challenge is a 64-byte random (octet-string). data ::= challenge challenge Data type: octet-string Authorized value: Decoded as Hexa (Size = 64) Upon invocation of this method, the meter will generate a response to the challenge by performing an HMAC-SHA256(K, m) where K = the AK of the corresponding client and m is the concatenation of Server System Title, Client System Title, received challenge and the frame counter (SysT-S ¦¦ SysT-C ¦¦ Challenge ¦¦ FC) to be returned. data ::= structure { challenge_response: frame_counter: } challenge_response The challenge response value Data type: octet-string Authorized value: Decoded as Hexa (Size = 32) frame_counter: The actual frame counter value Data type: unsigned32 Authorised values: 0x00000000 … 0xFFFFFFFF
x | x | x | x
x | x |  |  |  | Association LN - PLC Management Client |  | 15 | 3 | 0-0:40.0.4.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "0000280004FF" | -- | -- | -- | Get | -- | -- | Get | Get
x | x |  |  | 2 | object_list | object_list_type |  |  |  | -- | -- | -- | Get | -- | -- | Get | Get
x | x |  |  | 3 | associated_partners_id | associated_partners_type |  |  |  | -- | -- | -- | Get | -- | -- | Get | Get
x | x |  |  | 4 | application_context_name | application_context_name |  |  | "60857405080103" | -- | -- | -- | Get | -- | -- | Get | Get | Logical_Name_Referencing_With_Ciphering ::= context_id(3)
x | x |  |  | 5 | xDLMS_context_info | xDLMS_context_type |  |  |  | -- | -- | -- | Get | -- | -- | Get | Get
x | x |  |  | 6 | authentication_mechanism_name | mechanism_name_structure |  |  | "60857405080207" | -- | -- | -- | Get | -- | -- | Get | Get | HLS mechanism_id 7 (ECDSA)
x | x |  |  | 7 | secret | octet_string |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x |  |  | 8 | association_status | enum |  |  |  | -- | -- | -- | Get | -- | -- | Get | Get
x | x |  |  | 9 | security_setup_reference | octet_string[6] |  |  | "00002B0004FF" | -- | -- | -- | Get | -- | -- | Get | Get
x | x |  |  | 10 | user_list | array (user_list_entry) |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x |  |  | 11 | current_user | user_list_entry |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x |  |  | 1 | reply_to_HLS_authentication |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | This method is only applicable to teh 'Current Association' object
x | x |  |  | 2 | change_HLS_secret |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | The new HLS secret is not used with HLS mechanism_id 7 (ECDSA)
x | x |  |  | 3 | add_object |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x |  |  | 4 | remove_object |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x |  |  | 5 | add_user |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x |  |  | 6 | remove_user |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x
x | x |  |  |  | Security setup - PLC Management Client |  | 64 | 1 | 0-0:43.0.4.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00002B0004FF" | -- | -- | -- | Get | -- | -- | Get | Get
x | x |  |  | 2 | security_policy | enum |  |  | 0x6C | -- | -- | -- | Get | -- | -- | Get | Get | Bit Security policy 0 unused, shall be set to 0, 1 unused, shall be set to 0, 2 authenticated request, 3 encrypted request, 4 digitally signed request, 5 authenticated response, 6 encrypted response, 7 digitally signed response
x | x |  |  | 3 | security_suite | enum |  |  | 1 | -- | -- | -- | Get, Set | -- | -- | Get, Set Req S, Res - | Get, Set Req S, Res - | Strengthening the security suite means that the level of protection is increase. Once the protection is increased, it cannot be lowered. allowed range 1 = AES-GCM-128, ECDSA P-256, ECDH P-256, SHA-256, V.44, AES-128 2 = optional until Security suite 2 is available
x | x |  |  | 4 | client_system_title | octet_string[8] |  |  |  | -- | -- | -- | Get | -- | -- | Get | Get
x | x |  |  | 5 | server_system_title | octet_string[8] |  |  |  | -- | -- | -- | Get | -- | -- | Get | Get
x | x |  |  | 6 | certificates | array(certificate_info) |  |  |  | -- | -- | -- | Get | -- | -- | Get | Get | For the server: – Digital Signature Certificate For client: – Digital Signature Certificate 1 – Digital Signature Certificate 2 For Certification Authorities: – Sub-CA 3 (DLMS Client) - Digital Signature Certificate
x | x |  |  | 1 | security_activate | enum |  |  |  | -- | -- | -- | Action | -- | -- | Action Req S, Res - | Action Req S, Res - | Activates and strengthens the security policy: Strengthening the security policy means that another kind of protection is added. Once a kind of protection is added, it cannot be removed. If the method is invoked with a value indicating a security policy that is weaker than the value of the security_policy attribute, the method invocation fails. The new security policy applies as soon as the method invocation has been confirmed with success. as specified at the security_policy attribute. allowed range: (Bit Security policy) 0 unused, shall be set to 0, 1 unused, shall be set to 0, 2 authenticated request, 3 encrypted request, 4 digitally signed request, 5 authenticated response, 6 encrypted response, 7 digitally signed response
x | x |  |  | 2 | global_key_transfer | key_data |  |  |  | -- | -- | -- | Action | -- | -- | -- | -- | allowed range: (0) global unicast encryption key, (2) authentication key,
x | x |  |  | 3 | key_argeement | key_agreement |  |  |  | -- | -- | -- | -- | -- | -- | Action Req S, Res - | Action Req S, Res - | allowed range: (0) global unicast encryption key, (2) authentication key,
x | x |  |  | 4 | generate_key_pair | enum |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x |  |  | 5 | generate_certificate_request | enum |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x |  |  | 6 | import_certificate | octet_string |  |  |  | -- | -- | -- | Action | -- | -- | Action Req S, Res - | Action Req S, Res - | Imports an X.509 v3 certificate of a public key. allowed range: For client: – Digital Signature Certificate 1 – Digital Signature Certificate 2
x | x |  |  | 7 | export_certificate | octet_string |  |  |  | -- | -- | -- | Action | -- | -- | Action Req S, Res - | Action Req S, Res - | Exports an X.509 v3 certificate in the server. allowed range: For the server: – Digital Signature Certificate For client: – Digital Signature Certificate 1 – Digital Signature Certificate 2 For Certification Authorities: – Sub-CA 2 (DLMS Client) - Digital Signature Certificate
x | x |  |  | 8 | remove_certificate | octet_string |  |  |  | -- | -- | -- | Action | -- | -- | Action Req S, Res - | Action Req S, Res - | Removes X.509 v3 certificate in the server. allowed range: For client: – Digital Signature Certificate 1 – Digital Signature Certificate 2
x | x
x | x |  |  |  | Rx frame counter - unicast key - PLC Management Client |  | 12544 | 0 | 0-0:43.1.4.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00002B0104FF" | Get | -- | -- | Get | -- | -- | Get | Get
x | x |  |  | 1 | get_frame_counter | octet_string[64] |  |  |  | Action | -- | -- | Action | -- | -- | Action | Action | Method 1: get_frame_counter (data) The challenge is a 64-byte random (octet-string). data ::= challenge challenge Data type: octet-string Authorized value: Decoded as Hexa (Size = 64) Upon invocation of this method, the meter will generate a response to the challenge by performing an HMAC-SHA256(K, m) where K = the AK of the corresponding client and m is the concatenation of Server System Title, Client System Title, received challenge and the frame counter (SysT-S ¦¦ SysT-C ¦¦ Challenge ¦¦ FC) to be returned. data ::= structure { challenge_response: frame_counter: } challenge_response The challenge response value Data type: octet-string Authorized value: Decoded as Hexa (Size = 32) frame_counter: The actual frame counter value Data type: unsigned32 Authorised values: 0x00000000 … 0xFFFFFFFF
x | x
x | x | x | x |  | Association LN - - Installation Client |  | 15 | 3 | 0-0:40.0.5.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000280005FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | object_list | object_list_type |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 3 | associated_partners_id | associated_partners_type |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 4 | application_context_name | application_context_name |  |  | "60857405080103" | -- | -- | -- | Get | -- | -- | -- | Get | Logical_Name_Referencing_With_Ciphering ::= context_id(3)
x | x | x | x | 5 | xDLMS_context_info | xDLMS_context_type |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 6 | authentication_mechanism_name | mechanism_name_structure |  |  | "60857405080206" | -- | -- | -- | Get | -- | -- | -- | Get | HLS mechanism_id 6 (SHA-256)
x | x | x | x | 7 | secret | octet_string |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 8 | association_status | enum |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 9 | security_setup_reference | octet_string[6] |  |  | "00002B0005FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 10 | user_list | array (user_list_entry) |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x | 11 | current_user | user_list_entry |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x | 1 | reply_to_HLS_authentication |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | This method is only applicable to teh 'Current Association' object
x | x | x | x | 2 | change_HLS_secret |  |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | The new HLS secret is keywrapped. The key wrapping algorithm is as specified by the security suite. The KEK is the master key. For HLS mode 6 (SHA-256) the new HLS secret length must be between 128bit (16byte) and 256bit (32byte)
x | x | x | x | 3 | add_object |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 4 | remove_object |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 5 | add_user |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x | 6 | remove_user |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x
x | x | x | x |  | Security setup - Installation Client |  | 64 | 1 | 0-0:43.0.5.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00002B0005FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | security_policy | enum |  |  | 0x6C | -- | -- | -- | Get | -- | -- | -- | Get | Bit Security policy 0 unused, shall be set to 0, 1 unused, shall be set to 0, 2 authenticated request, 3 encrypted request, 4 digitally signed request, 5 authenticated response, 6 encrypted response, 7 digitally signed response
x | x | x | x | 3 | security_suite | enum |  |  | 1 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set Req S, Res - | Strengthening the security suite means that the level of protection is increase. Once the protection is increased, it cannot be lowered. allowed range 1 = AES-GCM-128, ECDSA P-256, ECDH P-256, SHA-256, V.44, AES-128 2 = optional until Security suite 2 is available
x | x | x | x | 4 | client_system_title | octet_string[8] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 5 | server_system_title | octet_string[8] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 6 | certificates | array(certificate_info) |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 1 | security_activate | enum |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | Activates and strengthens the security policy: Strengthening the security policy means that another kind of protection is added. Once a kind of protection is added, it cannot be removed. If the method is invoked with a value indicating a security policy that is weaker than the value of the security_policy attribute, the method invocation fails. The new security policy applies as soon as the method invocation has been confirmed with success. as specified at the security_policy attribute. allowed range: (Bit Security policy) 0 unused, shall be set to 0, 1 unused, shall be set to 0, 2 authenticated request, 3 encrypted request, 4 digitally signed request, 5 authenticated response, 6 encrypted response, 7 digitally signed response
x | x | x | x | 2 | global_key_transfer | key_data |  |  |  | -- | -- | -- | Action | -- | -- | -- | -- | allowed range: (0) global unicast encryption key, (2) authentication key,
x | x | x | x | 3 | key_argeement | key_agreement |  |  |  | -- | -- | -- | -- | -- | -- | -- | Action Req S, Res - | allowed range: (0) global unicast encryption key, (2) authentication key,
x | x | x | x | 4 | generate_key_pair | enum |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 5 | generate_certificate_request | enum |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 6 | import_certificate | octet_string |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 7 | export_certificate |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 8 | remove_certificate |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Rx frame counter - unicast key - Installation Client |  | 12544 | 0 | 0-0:43.1.5.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00002B0105FF" | Get | -- | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | get_frame_counter | octet_string[64] |  |  |  | Action | -- | Action | Action | -- | -- | -- | Action | Method 1: get_frame_counter (data) The challenge is a 64-byte random (octet-string). data ::= challenge challenge Data type: octet-string Authorized value: Decoded as Hexa (Size = 64) Upon invocation of this method, the meter will generate a response to the challenge by performing an HMAC-SHA256(K, m) where K = the AK of the corresponding client and m is the concatenation of Server System Title, Client System Title, received challenge and the frame counter (SysT-S ¦¦ SysT-C ¦¦ Challenge ¦¦ FC) to be returned. data ::= structure { challenge_response: frame_counter: } challenge_response The challenge response value Data type: octet-string Authorized value: Decoded as Hexa (Size = 32) frame_counter: The actual frame counter value Data type: unsigned32 Authorised values: 0x00000000 … 0xFFFFFFFF
x | x | x | x
x | x | x | x |  | Association LN - Maintenance Client |  | 15 | 3 | 0-0:40.0.6.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000280006FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | object_list | object_list_type |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 3 | associated_partners_id | associated_partners_type |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 4 | application_context_name | application_context_name |  |  | "60857405080103" | -- | -- | -- | Get | -- | -- | -- | Get | Logical_Name_Referencing_With_Ciphering ::= context_id(3)
x | x | x | x | 5 | xDLMS_context_info | xDLMS_context_type |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 6 | authentication_mechanism_name | mechanism_name_structure |  |  | "60857405080206" | -- | -- | -- | Get | -- | -- | -- | Get | HLS mechanism_id 6 (SHA-256)
x | x | x | x | 7 | secret | octet_string |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 8 | association_status | enum |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 9 | security_setup_reference | octet_string[6] |  |  | "00002B0006FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 10 | user_list | array (user_list_entry) |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x | 11 | current_user | user_list_entry |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x | 1 | reply_to_HLS_authentication |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | This method is only applicable to teh 'Current Association' object
x | x | x | x | 2 | change_HLS_secret |  |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | The new HLS secret is keywrapped. The key wrapping algorithm is as specified by the security suite. The KEK is the master key. For HLS mode 6 (SHA-256) the new HLS secret length must be between 128bit (16byte) and 256bit (32byte)
x | x | x | x | 3 | add_object |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 4 | remove_object |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 5 | add_user |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x | 6 | remove_user |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x
x | x | x | x |  | Security setup - Maintenance Client |  | 64 | 1 | 0-0:43.0.6.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00002B0006FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | security_policy | enum |  |  | 0x6C | -- | -- | -- | Get | -- | -- | -- | Get | Bit Security policy 0 unused, shall be set to 0, 1 unused, shall be set to 0, 2 authenticated request, 3 encrypted request, 4 digitally signed request, 5 authenticated response, 6 encrypted response, 7 digitally signed response
x | x | x | x | 3 | security_suite | enum |  |  | 1 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set Req S, Res - | Strengthening the security suite means that the level of protection is increase. Once the protection is increased, it cannot be lowered. allowed range 1 = AES-GCM-128, ECDSA P-256, ECDH P-256, SHA-256, V.44, AES-128 2 = optional until Security suite 2 is available
x | x | x | x | 4 | client_system_title | octet_string[8] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 5 | server_system_title | octet_string[8] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 6 | certificates | array(certificate_info) |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 1 | security_activate | enum |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | Activates and strengthens the security policy: Strengthening the security policy means that another kind of protection is added. Once a kind of protection is added, it cannot be removed. If the method is invoked with a value indicating a security policy that is weaker than the value of the security_policy attribute, the method invocation fails. The new security policy applies as soon as the method invocation has been confirmed with success. as specified at the security_policy attribute. allowed range: (Bit Security policy) 0 unused, shall be set to 0, 1 unused, shall be set to 0, 2 authenticated request, 3 encrypted request, 4 digitally signed request, 5 authenticated response, 6 encrypted response, 7 digitally signed response
x | x | x | x | 2 | global_key_transfer | key_data |  |  |  | -- | -- | -- | Action | -- | -- | -- | -- | allowed range: (0) global unicast encryption key, (2) authentication key,
x | x | x | x | 3 | key_argeement | key_agreement |  |  |  | -- | -- | -- | -- | -- | -- | -- | Action Req S, Res - | allowed range: (0) global unicast encryption key, (2) authentication key,
x | x | x | x | 4 | generate_key_pair | enum |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 5 | generate_certificate_request | enum |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 6 | import_certificate | octet_string |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 7 | export_certificate |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 8 | remove_certificate |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Rx frame counter - unicast key - Maintenance Client |  | 12544 | 0 | 0-0:43.1.6.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00002B0106FF" | Get | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 1 | get_frame_counter | octet_string[64] |  |  |  | Action | -- | -- | Action | -- | -- | -- | Action | Method 1: get_frame_counter (data) The challenge is a 64-byte random (octet-string). data ::= challenge challenge Data type: octet-string Authorized value: Decoded as Hexa (Size = 64) Upon invocation of this method, the meter will generate a response to the challenge by performing an HMAC-SHA256(K, m) where K = the AK of the corresponding client and m is the concatenation of Server System Title, Client System Title, received challenge and the frame counter (SysT-S ¦¦ SysT-C ¦¦ Challenge ¦¦ FC) to be returned. data ::= structure { challenge_response: frame_counter: } challenge_response The challenge response value Data type: octet-string Authorized value: Decoded as Hexa (Size = 32) frame_counter: The actual frame counter value Data type: unsigned32 Authorised values: 0x00000000 … 0xFFFFFFFF
x | x | x | x
x | x | x | x |  | Association LN - Certification Client |  | 15 | 3 | 0-0:40.0.7.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000280007FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | object_list | object_list_type |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 3 | associated_partners_id | associated_partners_type |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 4 | application_context_name | application_context_name |  |  | "60857405080103" | -- | -- | -- | Get | -- | -- | -- | Get | Logical_Name_Referencing_With_Ciphering ::= context_id(3)
x | x | x | x | 5 | xDLMS_context_info | xDLMS_context_type |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 6 | authentication_mechanism_name | mechanism_name_structure |  |  | "60857405080206" | -- | -- | -- | Get | -- | -- | -- | Get | HLS mechanism_id 6 (SHA-256)
x | x | x | x | 7 | secret | octet_string |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 8 | association_status | enum |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 9 | security_setup_reference | octet_string[6] |  |  | "00002B0007FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 10 | user_list | array (user_list_entry) |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x | 11 | current_user | user_list_entry |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x | 1 | reply_to_HLS_authentication |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | This method is only applicable to teh 'Current Association' object
x | x | x | x | 2 | change_HLS_secret |  |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | The new HLS secret is keywrapped. The key wrapping algorithm is as specified by the security suite. The KEK is the master key. For HLS mode 6 (SHA-256) the new HLS secret length must be between 128bit (16byte) and 256bit (32byte)
x | x | x | x | 3 | add_object |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 4 | remove_object |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 5 | add_user |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x | 6 | remove_user |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not used - no access per default
x | x | x | x
x | x | x | x |  | Security setup - Certification Client |  | 64 | 1 | 0-0:43.0.7.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00002B0007FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | security_policy | enum |  |  | 0x6C | -- | -- | -- | Get | -- | -- | -- | Get | Bit Security policy 0 unused, shall be set to 0, 1 unused, shall be set to 0, 2 authenticated request, 3 encrypted request, 4 digitally signed request, 5 authenticated response, 6 encrypted response, 7 digitally signed response
x | x | x | x | 3 | security_suite | enum |  |  | 1 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set Req S, Res - | Strengthening the security suite means that the level of protection is increase. Once the protection is increased, it cannot be lowered. allowed range 1 = AES-GCM-128, ECDSA P-256, ECDH P-256, SHA-256, V.44, AES-128 2 = optional until Security suite 2 is available
x | x | x | x | 4 | client_system_title | octet_string[8] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 5 | server_system_title | octet_string[8] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 6 | certificates | array(certificate_info) |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 1 | security_activate | enum |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | Activates and strengthens the security policy: Strengthening the security policy means that another kind of protection is added. Once a kind of protection is added, it cannot be removed. If the method is invoked with a value indicating a security policy that is weaker than the value of the security_policy attribute, the method invocation fails. The new security policy applies as soon as the method invocation has been confirmed with success. as specified at the security_policy attribute. allowed range: (Bit Security policy) 0 unused, shall be set to 0, 1 unused, shall be set to 0, 2 authenticated request, 3 encrypted request, 4 digitally signed request, 5 authenticated response, 6 encrypted response, 7 digitally signed response
x | x | x | x | 2 | global_key_transfer | key_data |  |  |  | -- | -- | -- | Action | -- | -- | -- | -- | allowed range: (0) global unicast encryption key, (2) authentication key,
x | x | x | x | 3 | key_argeement | key_agreement |  |  |  | -- | -- | -- | -- | -- | -- | -- | Action Req S, Res - | allowed range: (0) global unicast encryption key, (2) authentication key,
x | x | x | x | 4 | generate_key_pair | enum |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 5 | generate_certificate_request | enum |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 6 | import_certificate | octet_string |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 7 | export_certificate |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 8 | remove_certificate |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Rx frame counter - unicast key - Certification Client |  | 12544 | 0 | 0-0:43.1.7.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00002B0107FF" | Get | -- | -- | Get | Get | -- | -- | Get
x | x | x | x | 1 | get_frame_counter | octet_string[64] |  |  |  | Action | -- | -- | Action | Action | -- | -- | Action | Method 1: get_frame_counter (data) The challenge is a 64-byte random (octet-string). data ::= challenge challenge Data type: octet-string Authorized value: Decoded as Hexa (Size = 64) Upon invocation of this method, the meter will generate a response to the challenge by performing an HMAC-SHA256(K, m) where K = the AK of the corresponding client and m is the concatenation of Server System Title, Client System Title, received challenge and the frame counter (SysT-S ¦¦ SysT-C ¦¦ Challenge ¦¦ FC) to be returned. data ::= structure { challenge_response: frame_counter: } challenge_response The challenge response value Data type: octet-string Authorized value: Decoded as Hexa (Size = 32) frame_counter: The actual frame counter value Data type: unsigned32 Authorised values: 0x00000000 … 0xFFFFFFFF
x | x | x | x
x | x | x | x |  | Abstract objects - ID's & Control information
x | x | x | x |  | COSEM logical device name |  | 1 | 0 | 0-0:42.0.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00002A0000FF" | Get | Get | Get | Get | Get | -- | Get | Get
x | x | x | x | 2 | value | octet_string[16] |  |  |  | Get | Get | Get | Get | Get | -- | Get | Get | unique identification of the logical device
x | x | x | x
x | x | x | x |  | Device ID 1, E-meter manufacturing number |  | 1 | 0 | 0-0:96.1.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600100FF" | Get | Get | Get | Get | Get | -- | Get | Get
x | x | x | x | 2 | value | octet_string[0..14] |  |  |  | Get | Get | Get | Get | Get | -- | Get | Get | E-meter - Identification number according DIN 43863-5 (This is a 14 -digit alphanumeric number sequence )
x | x | x | x
x | x | x | x |  | Device ID 2, Comms module manufacturing number |  | 1 | 0 | 0-0:96.1.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600101FF" | Get | Get | Get | Get | Get | -- | Get | Get
x | x | x | x | 2 | value | octet_string[0..14] |  |  |  | Get | Get | Get | Get | Get | -- | Get | Get | Communication Module - Identification number according DIN 43863-5 (This is a 14 -digit alphanumeric number sequence )
x | x | x | x
x | x | x | x |  | Parameter record number |  | 1 | 0 | 1-0:0.2.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100000201FF" | -- | Get | Get | Get | Get | -- | Get | Get
x | x | x | x | 2 | value | octet_string[0..8] |  |  |  | -- | Get | Get, Set | Get, Set | Get | -- | Get, Set | Get, Set | Parameter record number is used for the identification of the Configuration Set
x | x | x | x
x | x | x | x |  | Abstract objects - Time and Date
x | x | x | x |  | Clock |  | 8 | 0 | 0-0:1.0.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000010000FF" | -- | Get | Get | Get | Get | -- | Get | Get
x | x | x | x | 2 | time | octet_string[12] |  |  |  | -- | Get | Get, Set | Get, Set | Get, Set | -- | Get | Get, Set Req S, Res - | Current date and time as local time With Read - deviation can be handeled or set to 0x8000, status must be handled. With Set - hundreth, das of week, deviation and status must be ignored
x | x | x | x | 3 | time_zone | long |  |  | -60 | -- | Get | Get, Set | Get, Set | Get, Set | -- | Get | Get, Set Req S, Res - | Setting the deviation to -60 represents a local time of GMT+1
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | Get | -- | Get | Get
x | x | x | x | 5 | daylights_savings_begin | octet_string[12] |  |  | "FFFF03FE07020000008000FF" | -- | Get | Get, Set | Get, Set | Get, Set | -- | Get | Get, Set Req S, Res - | last sunday in March at 02:00
x | x | x | x | 6 | daylights_savings_end | octet_string[12] |  |  | "FFFF0AFE07030000008000FF" | -- | Get | Get, Set | Get, Set | Get, Set | -- | Get | Get, Set Req S, Res - | last sunday in October at 03:00
x | x | x | x | 7 | daylights_savings_deviation | integer |  |  | 60 | -- | Get | Get, Set | Get, Set | Get, Set | -- | Get | Get, Set Req S, Res - | set to 1h
x | x | x | x | 8 | daylights_savings_enabled | boolean |  |  | 1 | -- | Get | Get, Set | Get, Set | Get, Set | -- | Get | Get, Set Req S, Res - | DLS enabled by default
x | x | x | x | 9 | clock_base | enum |  |  | 1 | -- | Get | Get | Get | Get | -- | Get | Get | internal crystal (by default)
x | x | x | x |  | Local Time |  | 1 | 0 | 1-0:0.9.1.255 | [8 empty] | For display and readout purposes, not used for remote communication
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100000901FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | octet_string[4] |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x |  | Local Date |  | 1 | 0 | 1-0:0.9.2.255 | [8 empty] | For display and readout purposes, not used for remote communication
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100000902FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | octet_string[5] |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x |  | Clock Time Shift Limit |  | 3 | 0 | 1-0:0.9.11.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "010000090BFF" | -- | -- | -- | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | unsigned |  |  | 9 | -- | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set Req S, Res - | Maximum allowed time shift without registration of a time shift event default set to 9s
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,7} | -- | -- | -- | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x |  | Abstract objects - Tariffication
x | x | x | x |  | Tariffication Activity Calendar |  | 20 | 0 | 0-0:13.0.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000D0000FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | calendar_name_active | octet_string[0..8] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get | The calendar_name_active has a minimum size of 8 characters at least, i.e. [0..8] is mandatory but can be longer
x | x | x | x | 3 | season_profile_active | array[0..4..*] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 4 | week_profile_table_active | array[0..4..*] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 5 | day_profile_table_active | array[0..4..*] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 6 | calendar_name_passive | octet_string[0..8] |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | see calendar_name_active
x | x | x | x | 7 | season_profile_passive | array[0..4..*] |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 8 | week_profile_table_passive | array[0..4..*] |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 9 | day_profile_table_passive | array[0..4..*] |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 10 | activate_passive_calendar_time | octet_string[12] |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 1 | activate_passive_calendar | integer |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action
x | x | x | x |  | Tariffication Special Days Table |  | 11 | 0 | 0-0:11.0.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000B0000FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | entries | array[0..200..*] |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | minimum of 200 entries Default: empty array
x | x | x | x |  | Register activation - Energy |  | 6 | 0 | 0-0:14.0.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000E0001FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | register_assignment | array[0..*] |  |  | { {3,1-0:1.8.1.255}, {3,1-0:1.8.2.255} {3,1-0:2.8.1.255}, {3,1-0:2.8.2.255} {3,1-0:3.8.1.255}, {3,1-0:3.8.2.255} {3,1-0:4.8.1.255}, {3,1-0:4.8.2.255} } | -- | -- | -- | Get | -- | -- | -- | Get | Array size depends on the amount of rated registers supported; 32 mandatory, others optional
x | x | x | x | 3 | mask_list | array[0..*] |  |  | { T1, {1, 3, 5, 7}, T2, {2, 4 ,6 ,8} } | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 4 | active_mask | octet_string[0..8] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x |  | Register activation - Maximum Demand |  | 6 | 0 | 0-0:14.0.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000E0002FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | register_assignment | array[0..*](register_assignment_item) |  |  | { } | -- | -- | -- | Get | -- | -- | -- | Get | Array size depends on the amount of rated registers supported; 16 mandatory, others optional
x | x | x | x | 3 | mask_list | array[0..*] |  |  | { } | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 4 | active_mask | octet_string[0..8] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x |  | Tariffication script table |  | 9 | 0 | 0-0:10.0.100.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000A0064FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | scripts | scripts |  |  | { {1,{ {1,6,0-0:14.0.1.255,4,"T1"} } }, {2,{ {1,6,0-0:14.0.1.255,4,"T2"} } } } | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 1 | execute | long_unsigned |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Execute typically not needed since tariffication always controlled only internaly, never over remote communication.
x | x | x | x
x | x | x | x |  | Currently active energy tariff |  | 1 | 0 | 0-0:96.14.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600E00FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | octet_string[0..8] |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get | currently active tariff = active_mask of register activation object (mask_name of the 0-0:14.0.1.255) Empty octet string represents no tariff is active.
x | x | x | x
x | x | x | x |  | Default tariffication script |  | 1 | 0 | 0-0:96.14.15.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600E0FFF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  | 1 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | defines the default tariffication script in case of invalid tariffication, invalid clock of 'central'-tariffication scheme; carries the script selecor number to the lowest tariff (default tariff) allowed range - all defined scripts in attribute scripts of tariffication script table 0-0:10.0.100.255 - the value 0 is not allowed default value 1
x | x | x | x
x | x | x | x |  | Tariff Activation Event Log |  | 7 | 1 | 0-0:99.98.11.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "000063620BFF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.14.0.255,2,0}} | -- | Get | Get | Get | -- | -- | -- | Get | clock;Currently active energy tariff
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | asynchronously
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [30..*] | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res -
x | x | x | x
x | x | x | x |  | Abstract objects - Billing period reset
x | x | x | x |  | Predefined Scripts - MDI reset / end of billing period |  | 9 | 0 | 0-0:10.0.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000A0001FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | scripts | scripts |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Predefined Script - MDI reset / end of billing period
x | x | x | x | 1 | execute | long_unsigned |  |  | 1 | -- | -- | Action | Action | Action | -- | -- | Action | The activation of this scripts is performed by calling the execute() method to the script identifier 1 of the corresponding script object Triggering the demand reset by a remote command during the 15min reset lock ignores the request and generates an error response (other-reason)
x | x | x | x |  | End of billing period 1 scheduler |  | 22 | 0 | 0-0:15.0.0.255 | [8 empty] | Single action scheduler for Stored Billing Values Profile
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000F0000FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | executed_script | script22 |  |  | {0-0:10.0.1.255,1} | -- | -- | -- | Get | -- | -- | -- | Get | "MDI reset / end of billing period"
x | x | x | x | 3 | type | enum |  |  | 1 | -- | -- | -- | Get | -- | -- | -- | Get | 1 is mandatory (Other are optional)
x | x | x | x | 4 | execution_time | array[0..1](execution_time_date) |  |  | {{"00000000", "FFFFFF01FF"}} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | at midnight (or any other time) of the first day of every month; the execution can be disabled with writing empty array or {{"FFFFFFFF", "FFFFFFFFFF"}}
x | x | x | x |  | Ad-hoc End of billing period 1 scheduler |  | 22 | 0 | 0-0:15.1.0.255 | [8 empty] | Single action scheduler for Stored Billing Values Profile
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000F0100FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | executed_script | script22 |  |  | {0-0:10.0.1.255,1} | -- | -- | -- | Get | -- | -- | -- | Get | "MDI reset / end of billing period"
x | x | x | x | 3 | type | enum |  |  | 1 | -- | -- | -- | Get | -- | -- | -- | Get | 1 is mandatory (Other are optional)
x | x | x | x | 4 | execution_time | array[0..1](execution_time_date) |  |  | {} | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | and Date and Time setting is possible (no wildcads should be used) ; the execution can be disabled with writing empty array or {{"FFFFFFFF", "FFFFFFFFFF"}}
x | x | x | x |  | Data of billing period 1 |  | 7 | 1 | 0-0:98.1.0.255 | [8 empty] | Stored Billing Values Profile
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000620100FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[1..*](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0},{1,0-0:0.1.0.255,2,0}, {3,1-0:1.8.0.255,2,0}, {3,1-0:1.8.1.255,2,0}, {3,1-0:1.8.2.255,2,0}, {3,1-0:2.8.0.255,2,0}, {3,1-0:2.8.1.255,2,0}, {3,1-0:2.8.2.255,2,0}, {3,1-0:3.8.0.255,2,0}, {3,1-0:3.8.1.255,2,0}, {3,1-0:3.8.2.255,2,0}, {3,1-0:4.8.0.255,2,0}, {3,1-0:4.8.1.255,2,0}, {3,1-0:4.8.2.255,2,0}, {4,1-0:1.6.0.255,2,0}, {4,1-0:1.6.0.255,5,0}, {4,1-0:2.6.0.255,2,0}, {4,1-0:2.6.0.255,5,0} {4,1-0:3.6.0.255,2,0}, {4,1-0:3.6.0.255,5,0}, {4,1-0:4.6.0.255,2,0}, {4,1-0:4.6.0.255,5,0} {3,1-0:1.2.0.255,2,0}, {3,1-0:2.2.0.255,2,0}, {3,1-0:3.2.0.255,2,0}, {3,1-0:4.2.0.255,2,0}} | -- | Get | Get | Get | Get | -- | -- | Get | clock; counter; +A total; +A rate 1; +A rate 2; −A total; -A rate 1; -A rate 2; +R total; +R rate 1; +R rate 2; −R total; -R rate 1; -R rate 2; +P max+timestamp; -P max+timestamp; +Q max+timestamp; -Q max+timestamp
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | Get | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | Get | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [15..*] | -- | Get | Get | Get | Get | -- | -- | Get | ≥ 15 months
x | x | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 2 | capture |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x |  | Billing period counter |  | 1 | 0 | 0-0:0.1.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000000100FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get | Billing Period Counter valid range 00-99 => rollover to 00 after 99
x | x | x | x
x | x | x | x |  | Time stamp of the most recent billing period |  | 1 | 0 | 0-0:0.1.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000000102FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | octet_string[12] |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get | time of last billing closure; format same as clock.time
x | x | x | x
x | x | x | x |  | Abstract objects - Disconnector, Limiter
x | x | x | x |  | Disconnect control activity calendar |  | 20 | 0 | 0-0:13.0.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000D0001FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | calendar_name_active | octet_string[0..8] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get | The calendar_name_active has a minimum size of 8 characters at least, i.e. [0..8] is mandatory but can be longer
x | x | x | x | 3 | season_profile_active | array[0..4..*] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 4 | week_profile_table_active | array[0..4..*] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 5 | day_profile_table_active | array[0..4..*] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 6 | calendar_name_passive | octet_string[0..8] |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set Req S, Res - | see calendar_name_active
x | x | x | x | 7 | season_profile_passive | array[0..4..*] |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set Req S, Res -
x | x | x | x | 8 | week_profile_table_passive | array[0..4..*] |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set Req S, Res -
x | x | x | x | 9 | day_profile_table_passive | array[0..4..*] |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set Req S, Res -
x | x | x | x | 10 | activate_passive_calendar_time | octet_string[12] |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set Req S, Res -
x | x | x | x | 1 | activate_passive_calendar | integer |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res -
x | x | x | x
x | x | x | x |  | Disconnect control special days table |  | 11 | 0 | 0-0:11.0.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000B0001FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | entries | array[0..200..*] |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set Req S, Res - | minimum of 200 entries Default: empty array
x | x | x | x
x | x | x | x |  | Disconnect control scheduler |  | 22 | 0 | 0-0:15.0.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000F0001FF" | -- | -- | -- | -- | -- | -- | -- | Get
x | x | x | x | 2 | executed_script | script22 |  |  | {0-0:10.0.106.255, 3} | -- | -- | -- | -- | -- | -- | -- | Get, Set Req S, Res - | Connect or disconnect script of disconnector script table (0-0:10.0.106.255) Authorized value: 3 to 4 ( remote disconnection and reconnection)
x | x | x | x | 3 | type | enum |  |  | 1 | -- | -- | -- | -- | -- | -- | -- | Get | 1 is mandatory (others are optional. If only type 1 is supported Set is optional)
x | x | x | x | 4 | execution_time | array[0..1](execution_time_date) |  |  | {} | -- | -- | -- | -- | -- | -- | -- | Get, Set Req S, Res - | dedicated timepoint for connection or disconnection; the execution can be disabled with writing empty array or {{"FFFFFFFF", "FFFFFFFFFF"}}
x | x | x | x
x | x | x | x |  | Disconnect script table |  | 9 | 0 | 0-0:10.0.106.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000A006AFF" | -- | -- | -- | -- | -- | -- | -- | Get
x | x | x | x | 2 | scripts | array[4](script9) |  |  | { {1,{{1,70,0-0:96.3.10.255,3,2}}}, //set to ready_for_reconnection {2,{{1,70,0-0:96.3.10.255,3,1}}}, //set to connected {3,{{2,70,0-0:96.3.10.255,1,0}}}, //execute remote disconnect {4,{{2,70,0-0:96.3.10.255,2,0}}}, //execute remote connect } | -- | -- | -- | -- | -- | -- | -- | Get | connect and disconnect scripts, 1 and 2 model local disconnection and local reconnection, 3 and 4 model remote disconnection and connection
x | x | x | x | 1 | execute | long_unsigned |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Executes the script specified in parameter data. If data matches one of the script_identifiers in the script table, then the corresponding action_specification is executed. No direct method call possible via remote communication
x | x | x | x
x | x | x | x |  | Disconnect control |  | 70 | 0 | 0-0:96.3.10.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "000060030AFF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | output_state | boolean |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | control_state | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | control_mode | enum |  |  | 3 | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set Req S, Res - | Configures the behaviour of the disconnect control object for all triggers, i.e. the possible state transitions A control_mode change is only allowed if the current control_state is supported by the new control_mode. Authorised values: 0, 3 and 4
x | x | x | x | 1 | remote_disconnect | integer |  |  | 0 | -- | -- | Action | Action | -- | -- | -- | Action Req S, Res -
x | x | x | x | 2 | remote_connect | integer |  |  | 0 | -- | -- | Action | Action | -- | -- | -- | Action Req S, Res -
x | x | x | x
x | x | x | x |  | Event Object - Disconnect Control log |  | 1 | 0 | 0-0:96.11.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600B02FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255; at first power up or if no events were yet generated the value should return 255
x | x | x | x
x | x | x | x |  | Disconnect Control Log |  | 7 | 1 | 0-0:99.98.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000636202FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2..3](capture_object_definition) |  |  | {{8, 0-0:1.0.0.255, 2, 0}, {1, 0-0:96.11.2.255, 2, 0}, {71, 0-0:17.0.0.255, 3, 0}} | -- | Get | Get | Get | -- | -- | -- | Get | clock;control event code;limiter threshold
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | asynchronously
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [10..*] | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res -
x | x | x | x
x | x | x | x |  | Limiter import |  | 71 | 0 | 0-0:17.0.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000110000FF" | -- | -- | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | monitored_value | value_definition |  |  | {3, 1-0:1.7.0.255, 2} | -- | -- | Get | Get | -- | -- | -- | Get | Instantaneous active import power (+P)
x | x | x | x | 3 | threshold_active | threshold |  |  | 0 | -- | -- | Get | Get | -- | -- | -- | Get | Provides the active threshold value to which the attribute monitored is compared. The data type depends on the 'monitored value'. 0 = disabled (limiter can't exceed threshold)
x | x | x | x | 4 | threshold_normal | threshold |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set Req S, Res - | Provides the threshold value to which the attribute monitored is compared when in normal operation. The data type depends on the 'monitored value'. 0 = disabled (limiter can't exceed threshold) Data type: double_long_unsigned Authorized value: 0 to 0xFFFFFFFF Default value: 0
x | x | x | x | 5 | treshold_emergency | threshold |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set Req S, Res - | Provides the threshold value to which the attribute monitored is compared when an emergency profile is active. The data type depends on the 'monitored value' 0 = disabled (limiter can't exceed threshold) Data type: double_long_unsigned Authorized value: 0 to 0xFFFFFFFF Default value: 0
x | x | x | x | 6 | min_over_threshold_duration | double_long_unsigned |  |  | 180 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set Req S, Res - | Defines minimal over threshold duration in seconds required to execute the 'over threshold' action. Setting the delay to 0 inhibits the execution of the over threshold action. Data type: double_long_unsigned Authorized value: 0 to 900 Default value: 180
x | x | x | x | 7 | min_under_threshold_duration | double_long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set Req S, Res - | Defines minimal under threshold duration in seconds required to execute the 'under threshold' action. Setting the delay to 0 inhibits the execution of the under threshold action. Data type: double_long_unsigned Authorized value: 0 to 900 Default value: 0
x | x | x | x | 8 | emergency_profile | emergency_profile_type |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set Req S, Res - | empty = no emergency profile defined
x | x | x | x | 9 | emergency_profile_group_id_list | array |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set Req S, Res - | empty = no emergency ids defined
x | x | x | x | 10 | emergency_profile_active | boolean |  |  | 0 | -- | -- | Get | Get | -- | -- | -- | Get
x | x | x | x | 11 | actions | action_set |  |  | { {0-0:10.0.106.255,1} , {0-0:10.0.106.255,0}} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set Req S, Res -
x | x | x | x
x | x | x | x |  | Limiter export |  | 71 | 0 | 0-0:17.0.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000110001FF" | -- | -- | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | monitored_value | value_definition |  |  | {3, 1-0:2.7.0.255, 2} | -- | -- | Get | Get | -- | -- | -- | Get | Instantaneous active export power (-P)
x | x | x | x | 3 | threshold_active | threshold |  |  | 0 | -- | -- | Get | Get | -- | -- | -- | Get | Provides the active threshold value to which the attribute monitored is compared. The data type depends on the 'monitored value'. 0 = disabled (limiter can't exceed threshold)
x | x | x | x | 4 | threshold_normal | threshold |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set Req S, Res - | Provides the threshold value to which the attribute monitored is compared when in normal operation. The data type depends on the 'monitored value'. 0 = disabled (limiter can't exceed threshold) Data type: double_long_unsigned Authorized value: 0 to 0xFFFFFFFF Default value: 0
x | x | x | x | 5 | treshold_emergency | threshold |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set Req S, Res - | Provides the threshold value to which the attribute monitored is compared when an emergency profile is active. The data type depends on the 'monitored value' 0 = disabled (limiter can't exceed threshold) Data type: double_long_unsigned Authorized value: 0 to 0xFFFFFFFF Default value: 0
x | x | x | x | 6 | min_over_threshold_duration | double_long_unsigned |  |  | 180 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set Req S, Res - | Defines minimal over threshold duration in seconds required to execute the 'over threshold' action. Setting the delay to 0 inhibits the execution of the over threshold action. Data type: double_long_unsigned Authorized value: 0 to 900 Default value: 180
x | x | x | x | 7 | min_under_threshold_duration | double_long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set Req S, Res - | Defines minimal under threshold duration in seconds required to execute the 'under threshold' action. Setting the delay to 0 inhibits the execution of the under threshold action. Data type: double_long_unsigned Authorized value: 0 to 900 Default value: 0
x | x | x | x | 8 | emergency_profile | emergency_profile_type |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set Req S, Res - | empty = no emergency profile defined
x | x | x | x | 9 | emergency_profile_group_id_list | array |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set Req S, Res - | empty = no emergency ids defined
x | x | x | x | 10 | emergency_profile_active | boolean |  |  | 0 | -- | -- | Get | Get | -- | -- | -- | Get
x | x | x | x | 11 | actions | action_set |  |  | { {0-0:10.0.106.255,1} , {0-0:10.0.106.255,0}} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set Req S, Res -
x | x | x | x
x | x | x | x |  | Abstract objects - Load management
x | x | x | x |  | Load Mgmt activity calendar |  | 20 | 0 | 0-0:13.0.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000D0002FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | calendar_name_active | octet_string[0..8] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get | The calendar_name_active has a minimum size of 8 characters at least, i.e. [0..8] is mandatory but can be longer
x | x | x | x | 3 | season_profile_active | array[0..4..*] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 4 | week_profile_table_active | array[0..4..*] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 5 | day_profile_table_active | array[0..4..*] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 6 | calendar_name_passive | octet_string[0..8] |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | see calendar_name_active
x | x | x | x | 7 | season_profile_passive | array[0..4..*] |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 8 | week_profile_table_passive | array[0..4..*] |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 9 | day_profile_table_passive | array[0..4..*] |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 10 | activate_passive_calendar_time | octet_string[12] |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 1 | activate_passive_calendar | integer |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | Load Mgmt special days table |  | 11 | 0 | 0-0:11.0.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000B0002FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | entries | array[0..60..*] |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | minimum of 60 entries Default: empty array
x | x | x | x
x | x | x | x |  | Load Mgmt script table |  | 9 | 0 | 0-0:10.0.103.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000A0067FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | scripts | array[4..*](script9) |  |  | { {1,{{1,70,0-1:96.3.10.255,3,2}}}, {2,{{1,70,0-1:96.3.10.255,3,1}}}, {3,{{2,70,0-1:96.3.10.255,1,0}}}, {4,{{2,70,0-1:96.3.10.255,2,0}}}, ... } | -- | -- | -- | Get | -- | -- | -- | Get | connect and disconnect methods of the load mgmt objects (relays), see also disconnector script table for further details
x | x | x | x | 1 | execute | long_unsigned |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Executes the script specified in parameter data. If data matches one of the script_identifiers in the script table, then the corresponding action_specification is executed. No direct method call possible via remote communication
x | x | x | x
x | x | x | x |  | Load Mgmt - Relay control 1 |  | 70 | 0 | 0-1:96.3.10.255 | [8 empty] | Channel (filed B) to be incremented if additional instances needed
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "000160030AFF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | output_state | boolean |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | control_state | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | control_mode | enum |  |  | 4 | -- | Get | Get | Get | -- | -- | -- | Get | If only one control mode is supported then control mode shall be 6. If more than one mode is supported then optional Set should be allowed. For relay only mode 4 or 6 should be used.
x | x | x | x | 1 | remote_disconnect | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action Req S, Res -
x | x | x | x | 2 | remote_connect | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action Req S, Res -
x | x | x | x
x | x | x | x |  | Abstract objects - Errors & Alarms, Event logs
x | x | x | x |  | Error Register |  | 1 | 0 | 0-0:97.97.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000616100FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get, Set | Get | -- | -- | Get, Set
x | x | x | x
x | x | x | x |  | Fatal Error Register |  | 1 | 0 | 0-0:97.97.128.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000616180FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get | Any error in this register is considered as legally relevant and causes the cancellation of its metrological certification. The bit-allocation in this Fatal Error Register is manufacturer specific. Resetting is not permitted
x | x | x | x
x | x | x | x |  | Alarm Register 1 |  | 1 | 0 | 0-0:97.98.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000616200FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get, Set | Get | -- | -- | Get, Set
x | x | x | x
x | x | x | x |  | Alarm Filter 1 |  | 1 | 0 | 0-0:97.98.10.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "000061620AFF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  | 0xFFFF | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | This filter defines, if an event is handled as an alarm when it appears
x | x | x | x
x | x | x | x |  | Alarm Descriptor 1 |  | 1 | 0 | 0-0:97.98.20.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000616214FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | Updated on Alarm register change i.e. on 0->1 transition of any of the bits in Alarm register the corresponding bit in the Alarm descriptor is set
x | x | x | x
x | x | x | x |  | Alarm Monitor 1 |  | 21 | 0 | 0-0:16.1.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000100100FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | thresholds | array[1](double_long_unsigned) |  |  | {0} | -- | -- | -- | Get | -- | -- | -- | Get | Monitored value is Alarm descriptor 1. Value 0 in threshold means if any of the bits in monitor value is newly triggered the action of the monitor will be set.
x | x | x | x | 3 | monitored_value | value_definition |  |  | {1, 0-0:97.98.20.255, 2} | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 4 | actions | array[1](action_set) |  |  | {{{0-0:10.0.108.255,4} , {0-0:10.0.108.255,0}}} | -- | -- | -- | Get | -- | -- | -- | Get | triggers push on alarm in case of occurence, no action is triggered in case the alarm descriptor is cleared
x | x | x | x
x | x | x | x |  | Alarm Register 2 |  | 1 | 0 | 0-0:97.98.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000616201FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get, Set | Get | -- | -- | Get, Set
x | x | x | x
x | x | x | x |  | Alarm Filter 2 |  | 1 | 0 | 0-0:97.98.11.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "000061620BFF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  | 0xFFFF | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | This filter defines, if an event is handled as an alarm when it appears
x | x | x | x
x | x | x | x |  | Alarm Descriptor 2 |  | 1 | 0 | 0-0:97.98.21.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000616215FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | Updated on Alarm register change i.e. on 0->1 transition of any of the bits in Alarm register the corresponding bit in the Alarm descriptor is set
x | x | x | x
x | x | x | x |  | Alarm Monitor 2 |  | 21 | 0 | 0-0:16.1.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000100101FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | thresholds | array[1](double_long_unsigned) |  |  | {0} | -- | -- | -- | Get | -- | -- | -- | Get | Monitored value is Alarm descriptor 2. Value 0 in threshold means if any of the bits in monitor value is newly triggered the action of the monitor will be set.
x | x | x | x | 3 | monitored_value | value_definition |  |  | {1, 0-0:97.98.21.255, 2} | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 4 | actions | array[1](action_set) |  |  | {{{0-0:10.0.108.255,4} , {0-0:10.0.108.255,0}}} | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | triggers push on alarm in case of occurence, no action is triggered in case the alarm descriptor is cleared
x | x | x | x
x | x | x | x |  | Alarm Register 3 |  | 1 | 0 | 0-0:97.98.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000616202FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get, Set | Get | -- | -- | Get, Set
x | x | x | x
x | x | x | x |  | Alarm Filter 3 |  | 1 | 0 | 0-0:97.98.12.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "000061620CFF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  | 0xFF7F | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | This filter defines, if an event is handled as an alarm when it appears
x | x | x | x
x | x | x | x |  | Alarm Descriptor 3 |  | 1 | 0 | 0-0:97.98.22.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000616216FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | Updated on Alarm register change i.e. on 0->1 transition of any of the bits in Alarm register the corresponding bit in the Alarm descriptor is set
x | x | x | x
x | x | x | x |  | Alarm Monitor 3 |  | 21 | 0 | 0-0:16.1.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000100102FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | thresholds | array[1](double_long_unsigned) |  |  | {0} | -- | -- | -- | Get | -- | -- | -- | Get | Monitored value is Alarm descriptor 3. Value 0 in threshold means if any of the bits in monitor value is newly triggered the action of the monitor will be set.
x | x | x | x | 3 | monitored_value | value_definition |  |  | {1, 0-0:97.98.22.255, 2} | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 4 | actions | array[1](action_set) |  |  | {{{0-0:10.0.108.255,4} , {0-0:10.0.108.255,0}}} | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | triggers push on alarm in case of occurence, no action is triggered in case the alarm descriptor is cleared
x | x | x | x
x | x | x | x |  | Event Object - Standard Event Log |  | 1 | 0 | 0-0:96.11.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600B00FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
x | x | x | x
x | x | x | x |  | Standard Event Log |  | 7 | 1 | 0-0:99.98.0.255 | [8 empty] | Standard event log containing errors and alarms
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000636200FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.11.0.255,2,0}} | -- | Get | Get | Get | -- | -- | -- | Get | clock;event code
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | asynchronously
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [100..*] | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res -
x | x | x | x
x | x | x | x |  | Event Object - Fraud Detection Log |  | 1 | 0 | 0-0:96.11.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600B01FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
x | x | x | x
x | x | x | x |  | Fraud Detection Log |  | 7 | 1 | 0-0:99.98.1.255 | [8 empty] | Event log containing all fraud detection events
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000636201FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.11.1.255,2,0}} | -- | Get | Get | Get | -- | -- | -- | Get | clock;tamper event code
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | asynchronously
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [30..*] | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res -
x | x | x | x
x | x | x | x |  | Event Object - Communication Event Log |  | 1 | 0 | 0-0:96.11.5.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600B05FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
x | x | x | x
x | x | x | x |  | Communication Event Log |  | 7 | 1 | 0-0:99.98.5.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000636205FF" | -- | Get | Get | Get | -- | -- | Get | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | Get | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.11.5.255,2,0}} | -- | Get | Get | Get | -- | -- | Get | Get | clock;communication event code
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | Get | Get | asynchronously
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | Get | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | Get | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | Get | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [100..*] | -- | Get | Get | Get | -- | -- | Get | Get
x | x | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res -
x | x | x | x
x | x | x | x |  | Event Object - Communication Session Log |  | 1 | 0 | 0-0:96.11.6.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600B06FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | enum |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
x | x | x | x
x | x | x | x |  | Communication Session Log |  | 7 | 1 | 0-0:99.98.6.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000636206FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.11.6.255,2,0}, {15,0-0:40.0.0.255,3,0}, {64,0-0:43.0.0.255,4,0} }} | -- | Get | Get | Get | -- | -- | -- | Get | clock;communication event code; client_SAP/server_SAP; client system title
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | asynchronously
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [100..*] | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res -
x | x | x | x
x | x | x | x |  | Configuration Event Detail |  | 1 | 0 | 0-0:96.43.150.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000602B96FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | config_identification::= structure { service_id: enum, class_id: long-unsigned, logical_name: octet-string, index: integer } |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | Where: - the service_id element defines which action to be applied to the referenced object: (1) write attribute, (2) execute specific method - the index element defines (with service_id 1) which attribute of the selected object is affected; or (with service_id 2) which specific method is to be executed. The first attribute (logical_name) has index 1, the first specific method has index 1 as well.
x | x | x | x
x | x | x | x |  | Configuration Event Log |  | 7 | 1 | 0-0:99.98.10.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "000063620AFF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.43.150.255,2,0}} | -- | Get | Get | Get | -- | -- | -- | Get | clock; configuration event details
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | asynchronously
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [30..*] | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res -
x | x | x | x
x | x | x | x |  | Event Object - Security Event Log |  | 1 | 0 | 0-0:96.11.9.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600B09FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
x | x | x | x
x | x | x | x |  | Security Event Log |  | 7 | 1 | 0-0:99.98.9.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000636209FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range (including support for selected_ values) and per entry
x | x | x | x | 3 | capture_objects | array[2](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.11.9.255,2,0}, {15,0-0:40.0.0.255,3,0}, {64,0-0:43.0.0.255,4,0} } | -- | Get | Get | Get | -- | -- | -- | Get | clock; security event code; client SAP; server SAP; client system title
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | asynchronously
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [100..*] | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Security Group Event Counter Object - (G_EC_01) |  | 1 | 0 | 0-0:96.15.21.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600F15FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get | Registration of successful or failed authentication for a specific client (G_EC_01)
x | x | x | x
x | x | x | x |  | Security Group Event Counter Object - (G_EC_02) |  | 1 | 0 | 0-0:96.15.22.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600F16FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get | FW Upgrade (G_EC_02)
x | x | x | x
x | x | x | x |  | Security Group Event Counter Object - (G_EC_03) |  | 1 | 0 | 0-0:96.15.23.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600F17FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get | Manual change of date and time (G_EC_03)
x | x | x | x
x | x | x | x |  | Security Group Event Counter Object - (G_EC_04) |  | 1 | 0 | 0-0:96.15.24.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600F18FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get | Fraud attempts (G_EC_04)
x | x | x | x
x | x | x | x |  | Security Group Event Counter Object - (G_EC_05) |  | 1 | 0 | 0-0:96.15.25.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600F19FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get | Start-up, Reset or Reboot (G_EC_05)
x | x | x | x
x | x | x | x |  | Security Group Event Counter Object - (G_EC_06) |  | 1 | 0 | 0-0:96.15.26.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600F1AFF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get | Error and alarm register reset (G_EC_06)
x | x | x | x
x | x | x | x |  | Security Group Event Counter Object - (G_EC_07) |  | 1 | 0 | 0-0:96.15.26.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600F1AFF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get | Device specific failures (G_EC_07)
x | x | x | x
x | x | x | x |  | Security Group Event Counter Object - (G_EC_08) |  | 1 | 0 | 0-0:96.15.28.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600F1CFF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get | Reconfiguration of cryptographically relevant parameters (G_EC_08)
x | x | x | x
x | x | x | x |  | Security Group Event Counter Object - (G_EC_09) |  | 1 | 0 | 0-0:96.15.29.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600F1DFF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get | Disconnector specific events (G_EC_09)
x | x | x | x
x | x | x | x |  | Security Group Event Counter Object - (G_EC_10) |  | 1 | 0 | 0-0:96.15.30.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600F1EFF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get | Limiter specific events (G_EC_10)
x | x | x | x
x | x | x | x |  | Event Object - Certification Log |  | 1 | 0 | 0-0:96.11.98.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600B62FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
x | x | x | x
x | x | x | x |  | Certification Protected Event Log |  | 7 | 1 | 0-0:99.98.98.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000636262FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.11.98.255,2,0}, {64,0-0:43.0.0.255,4,0}, {1,1-0:0.2.0.255,2,0}} | -- | Get | Get | Get | -- | -- | -- | Get | clock;certification event code, client system title, active LR fw identifier
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | asynchronously
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [100..*] | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Abstract objects - User Interface
x | x | x | x |  | Consumer Message Code - Meter Display |  | 1 | 0 | 0-0:96.13.1.255 | [8 empty] | Consumer message code shown on meter's display
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600D01FF" | -- | -- | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | octet_string[0..64] |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set Req S, Res - | Message code to be shown on numeric display.
x | x | x | x
x | x | x | x |  | Push action scheduler - Consumer Information |  | 22 | 0 | 0-4:15.0.4.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00040F0004FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | executed_script | script22 |  |  | {0-0:10.0.108.255,8} | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 3 | type | enum |  |  | 5 | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 4 | execution_time | array[0..60](execution_time_date) |  |  | {} | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set Req S, Res - | up to 60 time execution time entries to allow a resotution of 1 second intervals. An empty array represents the deactivation of this interface. By default push is disabled.
x | x | x | x
x |  | x |  |  | Push setup - Consumer Information |  | 40 | 0 | 0-6:25.9.0.255
x |  | x |  | 1 | logical_name | octet_string[6] |  |  | "0006190900FF" | -- | -- | -- | Get | -- | -- | -- | Get
x |  | x |  | 2 | push_object_list | array[0..20..*](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,1,0}, {8,0-0:1.0.0.255,2,0}, {1,0-0:96.1.0.255,0,0}, {1,0-0:42.0.0.255,0,0}, {3,1-0:32.7.0.255,0,0}, {3,1-0:31.7.0.255,0,0}, {3,1-0:1.7.0.255,0,0}; {3,1-0:2.7.0.255,0,0}; {3,1-0:1.8.0.255,0,0}, {3,1-0:2.8.0.255,0,0},{3,1-0:3.8.0.255,0,0}, {3,1-0:4.8.0.255,0,0}} | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | Clock, attribute 2 – time Device ID 1 manufacturing number, attribute 2 – serial number COSEM logical device name, attribute 2 – logical device number Instantaneous voltage L1, attribute 0 – OBIS code, value, scalar and unit Instantaneous voltage L2, attribute 0 – OBIS code, value, scalar and unit Instantaneous voltage L3, attribute 0 – OBIS code, value, scalar and unit Instantaneous current L1, attribute 0 – OBIS code, value, scalar and unit Instantaneous current L2, attribute 0 – OBIS code, value, scalar and unit Instantaneous current L3, attribute 0 – OBIS code, value, scalar and unit Instantaneous active import power (+P), attribute 0 – OBIS code, value, scalar and unit Instantaneous active export power (-P), attribute 0 – OBIS code, value, scalar and unit Active energy import (+A), attribute 0 – OBIS code, value, scalar and unit Active energy export (-A), attribute 0 – OBIS code, value, scalar and unit Rective energy import (+R), attribute 0 – OBIS code, value, scalar and unit Rective energy export (-R), attribute 0 – OBIS code, value, scalar and unit
x |  | x |  | 3 | send_destination_and_method | send_destination_and_method_type |  |  | {201,"0002180600FF:FF:00",0} | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | Contains the destination address where the data specified by the push_object_list has to be sent, as well as the sending method. transport_service_type Data type: ENUM (201) manufacturer specific => DLMS via wired M-Bus Authorized value: 201 Default value: 201 Destination Data type: Octet String - OBIS code of the M-Bus master setup object - Link Layer Address (LLA) - Transport Layer Address (CI TL) Authorized value: "0002180600FF:FF:00" Default value: "0002180600FF:FF:00" message_type Data type: ENUM (0) A-XDR encoded xDLMS APDU Authorized value: 0 Default value: 0
x |  | x |  | 4 | communication_window | array[0..*](window_element) |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | delay in seconds between repetitions
x |  | x |  | 5 | randomisation_start_interval | long_unsigned |  |  | 0 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
x |  | x |  | 6 | number_of_retries | unsigned |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
x |  | x |  | 7 | repetition_delay | long_unsigned |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | Delay in seconds between repetitions
x |  | x |  | 1 | push | integer |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x |  | x
| x |  | x |  | Push setup - Consumer Information |  | 40 | 0 | 0-6:25.9.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0006190900FF" | -- | -- | -- | Get | -- | -- | -- | Get
| x |  | x | 2 | push_object_list | array[0..20..*](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,1,0}, {8,0-0:1.0.0.255,2,0}, {1,0-0:96.1.0.255,0,0}, {1,0-0:42.0.0.255,0,0}, {3,1-0:32.7.0.255,0,0}, {3,1-0:52.7.0.255,0,0}, {3,1-0:72.7.0.255,0,0}, {3,1-0:31.7.0.255,0,0}, {3,1-0:51.7.0.255,0,0}, {3,1-0:71.7.0.255,0,0}; {3,1-0:1.7.0.255,0,0}; {3,1-0:2.7.0.255,0,0}; {3,1-0:1.8.0.255,0,0}, {3,1-0:2.8.0.255,0,0},{3,1-0:3.8.0.255,0,0}, {3,1-0:4.8.0.255,0,0}} | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | Clock, attribute 2 – time Device ID 1 manufacturing number, attribute 2 – serial number COSEM logical device name, attribute 2 – logical device number Instantaneous voltage L1, attribute 0 – OBIS code, value, scalar and unit Instantaneous voltage L2, attribute 0 – OBIS code, value, scalar and unit Instantaneous voltage L3, attribute 0 – OBIS code, value, scalar and unit Instantaneous current L1, attribute 0 – OBIS code, value, scalar and unit Instantaneous current L2, attribute 0 – OBIS code, value, scalar and unit Instantaneous current L3, attribute 0 – OBIS code, value, scalar and unit Instantaneous active import power (+P), attribute 0 – OBIS code, value, scalar and unit Instantaneous active export power (-P), attribute 0 – OBIS code, value, scalar and unit Active energy import (+A), attribute 0 – OBIS code, value, scalar and unit Active energy export (-A), attribute 0 – OBIS code, value, scalar and unit Rective energy import (+R), attribute 0 – OBIS code, value, scalar and unit Rective energy export (-R), attribute 0 – OBIS code, value, scalar and unit
| x |  | x | 3 | send_destination_and_method | send_destination_and_method_type |  |  | {201,"0002180600FF:FF:00",0} | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | Contains the destination address where the data specified by the push_object_list has to be sent, as well as the sending method. transport_service_type Data type: ENUM (201) manufacturer specific => DLMS via wired M-Bus Authorized value: 201 Default value: 201 Destination Data type: Octet String - OBIS code of the M-Bus master setup object - Link Layer Address (LLA) - Transport Layer Address (CI TL) Authorized value: "0002180600FF:FF:00" Default value: "0002180600FF:FF:00" message_type Data type: ENUM (0) A-XDR encoded xDLMS APDU Authorized value: 0 Default value: 0
| x |  | x | 4 | communication_window | array[0..*](window_element) |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | delay in seconds between repetitions
| x |  | x | 5 | randomisation_start_interval | long_unsigned |  |  | 0 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
| x |  | x | 6 | number_of_retries | unsigned |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
| x |  | x | 7 | repetition_delay | long_unsigned |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | Delay in seconds between repetitions
| x |  | x | 1 | push | integer |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
x | x | x | x |  | Security setup - Consumer Information |  | 64 | 1 | 0-0:43.0.103.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00002B0067FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | security_policy | enum |  |  | 0x48 | -- | -- | -- | Get | -- | -- | -- | Get | Bit Security policy 0 unused, shall be set to 0, 1 unused, shall be set to 0, 2 authenticated request, 3 encrypted request, 4 digitally signed request, 5 authenticated response, 6 encrypted response, 7 digitally signed response
x | x | x | x | 3 | security_suite | enum |  |  | 1 | -- | -- | -- | Get,Set | -- | -- | -- | Get, Set Req S, Res - | Strengthening the security suite means that the level of protection is increase. Once the protection is increased, it cannot be lowered. allowed range 1 = AES-GCM-128, ECDSA P-256, ECDH P-256, SHA-256, V.44, AES-128 2 = optional until Security suite 2 is available
x | x | x | x | 4 | client_system_title | octet_string[8] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 5 | server_system_title | octet_string[8] |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 6 | certificates | array(certificate_info) |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 1 | security_activate | enum |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | Activates and strengthens the security policy: Strengthening the security policy means that another kind of protection is added. Once a kind of protection is added, it cannot be removed. If the method is invoked with a value indicating a security policy that is weaker than the value of the security_policy attribute, the method invocation fails. The new security policy applies as soon as the method invocation has been confirmed with success. as specified at the security_policy attribute. allowed range: (Bit Security policy) 0 unused, shall be set to 0, 1 unused, shall be set to 0, 2 authenticated request, 3 encrypted request, 4 digitally signed request, 5 authenticated response, 6 encrypted response, 7 digitally signed response
x | x | x | x | 2 | global_key_transfer | key_data |  |  |  | -- | -- | -- | Action | -- | -- | -- | -- | allowed range: (0) global unicast encryption key,
x | x | x | x | 3 | key_argeement | key_agreement |  |  |  | -- | -- | -- | -- | -- | -- | -- | Action Req S, Res - | allowed range: (0) global unicast encryption key,
x | x | x | x | 4 | generate_key_pair | enum |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 5 | generate_certificate_request | enum |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 6 | import_certificate | octet_string |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 7 | export_certificate |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 8 | remove_certificate |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | M-Bus master port setup - Consumer Information Interface |  | 74 | 0 | 0-2:24.6.0.255 | [8 empty] | Wired M-Bus port setup for Consumer Information Interface
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0002180600FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | comm_speed | enum |  |  | 3 | -- | -- | -- | Get | -- | -- | -- | Get | 3== 2400 bps fix
x | x | x | x
x | x | x | x |  | Load profile display control status |  | 1 | 0 | 0-0:96.5.4.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600504FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | unsigned |  |  | 3 | -- | Get | Get | Get | Get | -- | -- | Get | shows the current status for displaying the LP1 on the LCD: The status is defined as a bit field: Bit0: LP1 display status (0 = LP1 readout via display enabled/ 1= LP1 readout via display disabled) Bit1: LP2 display status (0 = LP2 readout via display enabled/ 1= LP2 readout via display disabled) Bit2: reserved Bit3: reserved Bit4: reserved Bit5: reserved Bit6: reserved Bit7: reserved Data type: UNSIGNED8 Authorized value: 0 to 3 Default value: 1 ( LP1 readout via display disabled)
x | x | x | x
x | x | x | x |  | Load profile display control schedule |  | 22 | 0 | 0-0:15.1.5.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000F0105FF" | -- | -- | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | executed_script | script22 |  |  | {0-0:10.1.109.255, [1..6]} | -- | -- | Get | Get, Set | Get, Set | -- | -- | Get, Set Req S, Res - | scripts of load profile display control script table (0-0:10.1.109.255)
x | x | x | x | 3 | type | enum |  |  | 1 | -- | -- | Get | Get | Get | -- | -- | Get | 1 is mandatory (Other are optional. If only type 1 is supported Set is optional)
x | x | x | x | 4 | execution_time | array[0..1](execution_time_date) |  |  | {} | -- | -- | Get, Set | Get, Set | Get, Set | -- | -- | Get, Set Req S, Res - | the execution can be disabled with writing empty array or {{"FFFFFFFF", "FFFFFFFFFF"}}
x | x | x | x
x | x | x | x |  | Load profile display control script table |  | 9 | 0 | 0-0:10.1.109.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000A016DFF" | -- | -- | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | scripts | scripts |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Predefined scripts for enabling or disabling the display of LP1 and LP2 on the LCD interface: 1: Enable the display of load profile 1 and 2 on the LCD 2: Disable the display of load profile 1 and 2 on the LCD 3: Enable the display of load profile 1 on the LCD 4: Disable the display of load profile 1 on the LCD 5: Enable the display of load profile 2 on the LCD 6: Disable the display of load profile 2 on the LCD
x | x | x | x | 1 | execute | long_unsigned |  |  |  | -- | -- | Action | Action | Action | -- | -- | Action Req S, Res - | The activation of this scripts is performed by calling the execute() method to the script identifier of the corresponding script object
x | x | x | x
x | x | x | x |  | Tariffication Scheme |  | 1 | 0 | 0-0:94.43.142.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00005E2B8EFF" | -- | -- | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | enum |  |  | 0 | -- | -- | Get, Set | Get, Set | Get, Set | -- | -- | Get, Set | defines the tariffication scheme to be used for the tariff rate indicators: Authorised values: 0 = ‘central’ tariffication scheme 1 = ‘rated’ tariffication scheme default: 0
x | x | x | x
x | x | x | x |  | General display readout (Data Scroll mode) |  | 7 | 1 | 0-0:21.0.1.255 | [8 empty] | List of the display data elements for the data scroll mode
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000150001FF" | -- | -- | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | -- | Get | Get | Get | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[1..50](capture_object_definition) |  |  | { {1,0-0:0.9.1.255,2,0}, {1,0-0:0.9.2.255,2,0}, {3,1-0:1.8.0.255,2,0}, } | -- | -- | Get, Set | Get, Set | Get, Set | -- | -- | Get, Set Req S, Res - | This object allows the configuration of the display elements shown in the Data Scroll Mode. Allowed range: please see 'Display Configuration' tab
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 5 | -- | -- | Get, Set | Get, Set | Get, Set | -- | -- | Get, Set Req S, Res - | auto scroll intervall in seconds a value of 0 prevents the display from scrolling
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | -- | Get | Get | Get | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | -- | Get | Get | Get | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | -- | Get | Get | Get | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | 1 | -- | -- | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Alternate display readout (Standard Data mode) |  | 7 | 1 | 0-0:21.0.2.255 | [8 empty] | List of the display data elements for the standard data mode
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000150002FF" | -- | -- | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | -- | Get | Get | Get | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[1..100](capture_object_definition) |  |  | { {1,0-0:0.9.1.255,2,0}, {1,0-0:0.9.2.255,2,0}, {1,0-0:96.1.0.255,2,0}, {1,0-0:0.1.2.101,2,0}, {1,0-0:0.1.2.102,2,0}, {3,1-0:1.8.0.255,2,0}, {3,1-0:1.8.0.101,2,0}, {3,1-0:1.8.0.102,2,0}, {3,1-0:1.8.1.255,2,0}, {3,1-0:1.8.1.101,2,0}, {3,1-0:1.8.1.102,2,0}, {3,1-0:1.8.2.255,2,0}, {3,1-0:1.8.2.101,2,0}, {3,1-0:1.8.2.102,2,0}, {3,1-0:2.8.0.255,2,0}, {3,1-0:2.8.0.101,2,0}, {3,1-0:2.8.0.102,2,0}, ........ {5,1-0:1.4.0.255,2,0}, {4,1-0:1.6.0.255,2,0}, {4,1-0:1.6.0.255,5,0}, {4,1-0:1.6.0.101,2,0}, {4,1-0:1.6.0.101,5,0}, {4,1-0:1.6.0.102,2,0}, {4,1-0:1.6.0.102,5,0}, {3,1-0:1.2.0.255,2,0}, {5,1-0:2.4.0.255,2,0}, {4,1-0:2.6.0.255,2,0}, {4,1-0:2.6.0.255,5,0}, {4,1-0:2.6.0.101,2,0}, {4,1-0:2.6.0.101,5,0}, {4,1-0:2.6.0.102,2,0}, {4,1-0:2.6.0.102,5,0}, {3,1-0:2.2.0.255,2,0}, ........ {1,1-0:0.2.0.255,2,0}, {1,1-0:0.2.8.255,2,0}, {1,1-1:0.2.0.255,2,0}, {1,1-1:0.2.8.255,2,0}, {1,1-2:0.2.0.255,2,0}, {1,1-2:0.2.8.255,2,0}, } | -- | -- | Get, Set | Get, Set | Get, Set | -- | -- | Get, Set Req S, Res - | This object allows the configuration of the display elements shown in the Standard Data Mode. The Standard Data typically contains the Device identification and billing relevant data Allowed range: please see 'Display Configuration' tab The Standard Data list contains the legally relevant data elements that must be available for verifying the customer’s billing data. Setting up this configuration must be in line with the MID and BEV certification requirements.
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | -- | Get | Get | Get | -- | -- | Get | asynchronously
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | -- | Get | Get | Get | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | -- | Get | Get | Get | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | -- | Get | Get | Get | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | 1 | -- | -- | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Alternate display readout (Service Data mode) |  | 7 | 1 | 0-0:21.0.3.255 | [8 empty] | List of the display data elements for the service data mode
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000150003FF" | -- | -- | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | -- | Get | Get | Get | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[1..100](capture_object_definition) |  |  | { {3,1-0:1.7.0.255,2,0}, {3,1-0:2.7.0.255,2,0}, {3,1-0:3.7.0.255,2,0}, {3,1-0:4.7.0.255,2,0}, {3,1-0:9.7.0.255,2,0}, {3,1-0:10.7.0.255,2,0}, {3,1-0:90.7.0.255,2,0}, {3,1-0:13.7.0.255,2,0}, {3,1-0:84.7.0.255,2,0}, {3,1-0:14.7.0.255,2,0}, {3,1-0:21.7.0.255,2,0}, {3,1-0:22.7.0.255,2,0}, {3,1-0:23.7.0.255,2,0}, {3,1-0:24.7.0.255,2,0}, {3,1-0:29.7.0.255,2,0}, {3,1-0:30.7.0.255,2,0}, {3,1-0:31.7.0.255,2,0}, {3,1-0:32.7.0.255,2,0}, {3,1-0:33.7.0.255,2,0}, {3,1-0:85.7.0.255,2,0}, {3,1-0:41.7.0.255,2,0}, {3,1-0:42.7.0.255,2,0}, {3,1-0:43.7.0.255,2,0}, {3,1-0:44.7.0.255,2,0}, {3,1-0:49.7.0.255,2,0}, {3,1-0:50.7.0.255,2,0}, {3,1-0:51.7.0.255,2,0}, {3,1-0:52.7.0.255,2,0}, {3,1-0:53.7.0.255,2,0}, {3,1-0:86.7.0.255,2,0}, {3,1-0:61.7.0.255,2,0}, {3,1-0:62.7.0.255,2,0}, {3,1-0:63.7.0.255,2,0}, {3,1-0:64.7.0.255,2,0}, {3,1-0:69.7.0.255,2,0}, {3,1-0:70.7.0.255,2,0}, {3,1-0:71.7.0.255,2,0}, {3,1-0:72.7.0.255,2,0}, {3,1-0:73.7.0.255,2,0}, {3,1-0:87.7.0.255,2,0}, {3,1-0:81.7.40.255,2,0}, {3,1-0:81.7.51.255,2,0}, {3,1-0:81.7.62.255,2,0}, } | -- | -- | Get, Set | Get, Set | Get, Set | -- | -- | Get, Set Req S, Res - | This object allows the configuration of the display elements shown in the Service Data Mode. The Service Data typically contains the Instantanious Values Allowed range: please see 'Display Configuration' tab
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | -- | Get | Get | Get | -- | -- | Get | asynchronously
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | -- | Get | Get | Get | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | -- | Get | Get | Get | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | -- | Get | Get | Get | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | 1 | -- | -- | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Abstract objects - Firmware Upgrade
x | x | x | x |  | Image transfer |  | 18 | 0 | 0-0:44.0.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00002C0000FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | image_block_size | double_long_unsigned |  |  | 96 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | block size in bytes valid range 64 to 1024
x | x | x | x | 3 | image_transferred_block_status | bit_string |  |  | 0 | -- | -- | -- | Get | -- | -- | -- | Get | each bit provides info about one individual image block 0 = not transferred 1 = transferred
x | x | x | x | 4 | image_first not_transferred_block_number | double_long_unsigned |  |  | 0 | -- | -- | -- | Get | -- | -- | -- | Get | provides block number of the first missing block
x | x | x | x | 5 | image_transfer_enabled | boolean |  |  | FALSE | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set Req S, Res - | enabled or not; detail information in image_transfer_status FALSE = disabled TRUE = enabled
x | x | x | x | 6 | image_transfer status | enum |  |  | 0 | -- | -- | -- | Get | -- | -- | -- | Get | detailed status of image transfer process 0 = transfer not initiated (not active; default state) 1 = transfer initiated 2 = verification initiated 3 = verification successful 4 = verification failed 5 = activation initiated 6 = activation successful 7 = activation failed
x | x | x | x | 7 | image_to_activate_info | array |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get | allows the retrieval of the digital signature after the image download and before the image activation.
x | x | x | x | 1 | image_transfer_initiate | structure |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action | initiates the transfer process; includes data in format { image_identifier image_size }
x | x | x | x | 2 | image_block_transfer | structure |  |  |  | -- | -- | -- | Action | -- | Action | -- | Action | transfers one single block; includes data in format { image_block_number image_block_value }
x | x | x | x | 3 | image_verify | integer |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action | verifies the integrity before activation; result can be (0) success, if the verification could be completed; (2) temporary-failure if the verification has not been completed; (250) other-reason if the verification failed.
x | x | x | x | 4 | image_activate | integer |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | activates the transferred and verified image; result can be (0) success, if the verification could be completed; (2) temporary-failure if the verification has not been completed; (250) other-reason if the verification failed.
x | x | x | x
x | x | x | x |  | Image transfer activation scheduler |  | 22 | 0 | 0-0:15.0.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000F0002FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | executed_script | script22 |  |  | {0-0:10.0.107.255,1} | -- | -- | -- | Get | -- | -- | -- | Get | activate image
x | x | x | x | 3 | type | enum |  |  | 1 | -- | -- | -- | Get | -- | -- | -- | Get | 1 is mandatory (Other are optional. If only type 1 is supported Set is optional)
x | x | x | x | 4 | execution_time | array[0..1](execution_time_date) |  |  | {} | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set Req S, Res - | the execution can be disabled with writing empty array or {{"FFFFFFFF", "FFFFFFFFFF"}}
x | x | x | x
x | x | x | x |  | Predefined Scripts - Image activation |  | 9 | 0 | 0-0:10.0.107.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000A006BFF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | scripts | scripts |  |  | {1,{ {2,18,0-0:44.0.0.255,4,0} } }, | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 1 | execute | long_unsigned |  |  | 1 | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res - | The activation of this scripts is performed by calling the execute() method to the script identifier 1 of the corresponding script object
x | x | x | x
x | x | x | x |  | Active firmware identifier |  | 1 | 0 | 1-0:0.2.0.255 | [8 empty] | B-field = 0: Metrologically relevant part of firmware
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100000200FF" | Get | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | octet_string |  |  |  | Get | Get | Get | Get | Get | -- | -- | Get
x | x | x | x
x | x | x | x |  | Active firmware signature |  | 1 | 0 | 1-0:0.2.8.255 | [8 empty] | B-field = 0: Metrologically relevant part of firmware
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100000208FF" | Get | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | octet_string |  |  |  | Get | Get | Get | Get | Get | -- | -- | Get
x | x | x | x
x | x | x | x |  | Active firmware identifier 1 |  | 1 | 0 | 1-1:0.2.0.255 | [8 empty] | B-field = 1: Application (metrologically non relevant part of firmware)
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0101000200FF" | Get | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | octet_string |  |  |  | Get | Get | Get | Get | Get | -- | -- | Get
x | x | x | x
x | x | x | x |  | Active firmware signature 1 |  | 1 | 0 | 1-1:0.2.8.255 | [8 empty] | B-field = 1: Application (metrologically non relevant part of firmware)
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0101000208FF" | Get | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | octet_string |  |  |  | Get | Get | Get | Get | Get | -- | -- | Get
x | x | x | x
x | x | x | x |  | Active firmware identifier 2 |  | 1 | 0 | 1-2:0.2.0.255 | [8 empty] | B-field = 2: 2=other parts (e.g. modem firmware)
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0102000200FF" | Get | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | octet_string |  |  |  | Get | Get | Get | Get | Get | -- | -- | Get
x | x | x | x
x | x | x | x |  | Active firmware signature 2 |  | 1 | 0 | 1-2:0.2.8.255 | [8 empty] | B-field = 2: 2=other parts (e.g. modem firmware)
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0102000208FF" | Get | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | octet_string |  |  |  | Get | Get | Get | Get | Get | -- | -- | Get
x | x | x | x
x | x | x | x |  | Abstract objects - Opt IN/OUT
x | x | x | x |  | Load profile control status |  | 1 | 0 | 0-0:96.5.3.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600503FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | unsigned |  |  | 0 | -- | Get | Get | Get | Get | -- | -- | Get | shows the current status of Opt IN/OUT status: The status is defined as a bit field: Bit0: LP1 status (0 = activated capturing in load profile 1 / 1= deactivated capturing in load profile 1) Bit1: LP2 status (0 = activated capturing in load profile 2 / 1= deactivated capturing in load profile 2) Bit2: reserved Bit3: reserved Bit4: reserved Bit5: reserved Bit6: reserved Bit7: reserved Data type: UNSIGNED8 Authorized value: 0 to 3 Default value: 0 (capturing of profiles LP1 and LP2 active)
x | x | x | x
x | x | x | x |  | Load profile control schedule |  | 22 | 0 | 0-0:15.0.5.255 | [8 empty] | Single action scheduler for Opt IN/OUT
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000F0005FF" | -- | -- | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | executed_script | script22 |  |  | {0-0:10.0.109.255, [1..6]} | -- | -- | Get, Set | Get, Set | Get, Set | -- | -- | Get, Set Req S, Res - | Opt IN/OUT scripts of load profile control script table (0-0:10.0.109.255)
x | x | x | x | 3 | type | enum |  |  | 1 | -- | -- | Get | Get | Get | -- | -- | Get | 1 is mandatory (Other are optional. If only type 1 is supported Set is optional)
x | x | x | x | 4 | execution_time | array[0..1](execution_time_date) |  |  | {} | -- | -- | Get, Set | Get, Set | Get, Set | -- | -- | Get, Set Req S, Res - | at midnight (or any other time) of the first day of every month; the execution can be disabled with writing empty array or {{"FFFFFFFF", "FFFFFFFFFF"}}
x | x | x | x
x | x | x | x |  | Load profile control script table |  | 9 | 0 | 0-0:10.0.109.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000A006DFF" | -- | -- | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | scripts | scripts |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Predefined scripts for the opt IN/OUT control of LP1 and LP2: 1: Activate the capturing in load profile 1 and 2 2: Deactivate the capturing in load profile 1 and 2 3: Activate the capturing in load profile 1 4: Deactivate the capturing in load profile 1 5: Activate the capturing in load profile 2 6: Deactivate the capturing in load profile 2
x | x | x | x | 1 | execute | long_unsigned |  |  |  | -- | -- | Action | Action | Action | -- | -- | Action Req S, Res - | The activation of this scripts is performed by calling the execute() method to the script identifier of the corresponding script object
x | x | x | x
x | x | x | x |  | Abstract objects - Certification support
x | x | x | x |  | Certification mode |  | 1 | 0 | 0-0:94.43.01.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00005E2B01FF" | -- | -- | -- | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | value ::= structure { certification_status: boolean; certification_energy_res: enum; certification_demand_res: enum; certification_LED_source: unsigned8; certification_LED_rate: unsigned16; } |  |  | {0;0;0;0;0} | -- | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set Req S, Res - | certification_status Activation or deactivation of the certification mode when writing this value. Reading this data shows the current activation status of the certification mode. Data type: Boolean Authorised values: 0: FALSE 1: TRUE Default value: 0 (FALSE) certification_energy_res: This items defines the resolution of the energy registers on the Display Data type: Enum Authorised values: 0: no change to the current settings 1: no decimals = x kWh 2: 1 decimal = x.1 kWh 3: 2 decimal = x.12 kWh 4: 3 decimal = x.123 kWh 5: 4 decimal = x.1234 kWh Default value: 0 (no change to the current settings) certification_demand_res: This items defines the resolution of the demand registers on the Display Data type: Enum Authorised values: 0: no change to the current resolution 1: no decimals = x kW 2: 1 decimal = x.1 kW 3: 2 decimal = x.12 kW 4: 3 decimal = x.123 kW 5: 4 decimal = x.1234 kW Default value: 0 (no change to the current settings) certification_LED_source: This item allows switching the energy source of the certification led. It’s possible to map up different energy types to this LED in order to allow combinations (like +/-A or +Q). The configuration item is defined as a bit field: Bit0: import active Bit1: export active Bit2: reactive Q1 Bit3: reactive Q2 Bit4: reactive Q3 Bit5: reactive Q4 Bit6: apparent import Bit7: apparent export Setting this value to 0 leaves the LED source setting untouched Data type: unsigned8 Authorised values: 0 to 0xFF Default value: 0 (no change to the current settings) certification_LED_rate: This items defines the pulse rate constant of the certification LED expressed in PULSES/kUNITh. The value of 0 leaves the LED pulse rate setting untouched Data type: unsigned16 Authorised values: 0, 1000, 2000, 4000, 8000, 16000 Default value: 0 (no change to the current settings)
x | x | x | x
x | x | x | x |  | Electricity related objects - Totals
x | x | x | x |  | Active energy import (+A) |  | 3 | 0 | 1-0:1.8.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100010800FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,30} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Active energy export (−A) |  | 3 | 0 | 1-0:2.8.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100020800FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,30} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Reactive energy import (+R) (QI+QII) |  | 3 | 0 | 1-0:3.8.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100030800FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,32} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Reactive energy export (-R) (QIII+QIV) |  | 3 | 0 | 1-0:4.8.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100040800FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,32} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Electricity related objects - Rated registers
x | x | x | x |  | Active energy import (+A) rate 1 |  | 3 | 0 | 1-0:1.8.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100010801FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,30} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Active energy import (+A) rate 2 |  | 3 | 0 | 1-0:1.8.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100010802FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,30} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Active energy export (−A) rate 1 |  | 3 | 0 | 1-0:2.8.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100020801FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,30} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Active energy export (−A) rate 2 |  | 3 | 0 | 1-0:2.8.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100020802FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,30} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Reactive energy (+R) rate 1 |  | 3 | 0 | 1-0:3.8.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100030801FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,32} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Reactive energy (+R) rate 2 |  | 3 | 0 | 1-0:3.8.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100030802FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,32} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Reactive energy (-R) rate 1 |  | 3 | 0 | 1-0:4.8.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100040801FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,32} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Reactive energy (-R) rate 2 |  | 3 | 0 | 1-0:4.8.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100040802FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,32} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Electricity related objects - Demand
x | x | x | x |  | Demand Register 1 - Active energy import (+A) |  | 5 | 0 | 1-0:1.4.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100010400FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | current_average_value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | last_average_value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 4 | scaler_unit | scal_unit_type |  |  | {0,27} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 5 | status | unsigned |  |  | 0 | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 6 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 7 | start_time_current | octet_string |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 8 | period | double_long_unsigned |  |  | 900 | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 9 | number_of_periods | long_unsigned |  |  | 1 | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 2 | next_period |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Demand Register 2 - Active energy export (−A) |  | 5 | 0 | 1-0:2.4.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100020400FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | current_average_value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | last_average_value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 4 | scaler_unit | scal_unit_type |  |  | {0,27} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 5 | status | unsigned |  |  | 0 | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 6 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 7 | start_time_current | octet_string |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 8 | period | double_long_unsigned |  |  | 900 | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 9 | number_of_periods | long_unsigned |  |  | 1 | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 2 | next_period |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Demand Register 3 - Reactive energy import (+R) |  | 5 | 0 | 1-0:3.4.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100030400FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | current_average_value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | last_average_value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 4 | scaler_unit | scal_unit_type |  |  | {0,29} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 5 | status | unsigned |  |  | 0 | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 6 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 7 | start_time_current | octet_string |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 8 | period | double_long_unsigned |  |  | 900 | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 9 | number_of_periods | long_unsigned |  |  | 1 | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 2 | next_period |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Demand Register 4 - Reactive energy export (-R) |  | 5 | 0 | 1-0:4.4.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100040400FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | current_average_value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | last_average_value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 4 | scaler_unit | scal_unit_type |  |  | {0,29} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 5 | status | unsigned |  |  | 0 | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 6 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 7 | start_time_current | octet_string |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 8 | period | double_long_unsigned |  |  | 900 | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 9 | number_of_periods | long_unsigned |  |  | 1 | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 2 | next_period |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Maximum Demand Register 1 - Active energy import (+A) |  | 4 | 0 | 1-0:1.6.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100010600FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,27} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Maximum Demand Register 6 - Active energy export (−A) |  | 4 | 0 | 1-0:2.6.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100020600FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,27} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Maximum Demand Register 11 - Reactive energy import (+R) |  | 4 | 0 | 1-0:3.6.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100030600FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,29} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Maximum Demand Register 16 - Reactive energy export (-R) |  | 4 | 0 | 1-0:4.6.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100040600FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,29} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Cumulative Maximum Demand Register 1 - Active energy import (+A) |  | 3 | 0 | 1-0:1.2.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100010200FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,27} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Cumulative Maximum Demand Register 6 - Active energy export (−A) |  | 3 | 0 | 1-0:2.2.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100020200FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,27} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Cumulative Maximum Demand Register 11 - Reactive energy import (+R) |  | 3 | 0 | 1-0:3.2.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100030200FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,29} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Cumulative Maximum Demand Register 16 - Reactive energy export (-R) |  | 3 | 0 | 1-0:4.2.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100040200FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,29} | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Electricity related objects - Profiles
x | x | x | x |  | Profile status - Load profile with period 1 |  | 1 | 0 | 0-0:96.10.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600A01FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | status | unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get | bitmask :: {PDN,reserved,CAD,CDI,DST,DNV,CIV,ERR}
x | x | x | x
x | x | x | x |  | Load profile with period 1 i.e. General Load Profile |  | 7 | 1 | 1-0:99.1.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100630100FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2..*](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0},{1,0-0:96.10.1.255,2,0},{3,1-0:1.8.0.255,2,0},{3,1-0:2.8.0.255,2,0},{3,1-0:3.8.0.255,2,0},{3,1-0:4.8.0.255,2,0}} | -- | Get | Get | Get | Get | -- | -- | Get | clock;AMR profile status; +A;−A;+Q;-Q
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 900 | -- | Get | Get | Get | Get | -- | -- | Get | 15 minutes
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | Get | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | Get | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | 5760 | -- | Get | Get | Get | Get | -- | -- | Get | 60 days with 15 min (exactly 5760 entries)
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 2 | capture |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Profile status - Load profile with period 2 |  | 1 | 0 | 0-0:96.10.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600A02FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | status | unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get | bitmask :: {PDN,reserved,CAD,CDI,DST,DNV,CIV,ERR}
x | x | x | x
x | x | x | x |  | Load profile with period 2 i.e. Daily Values Profile |  | 7 | 1 | 1-0:99.2.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100630200FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2..*](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.10.2.255,2,0}, {3,1-0:1.8.0.255,2,0}, {3,1-0:2.8.0.255,2,0}, {3,1-0:3.8.0.255,2,0}, {3,1-0:4.8.0.255,2,0}} | -- | Get | Get | Get | Get | -- | -- | Get | clock;AMR profile status; +A total; -A total, +A rate 1; +A rate 2
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 86400 | -- | Get | Get | Get | Get | -- | -- | Get | daily
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | Get | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | Get | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | 60 | -- | Get | Get | Get | Get | -- | -- | Get | 60 days with hourly entries (exactly 60 entries)
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x | 2 | capture |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Electricity related objects - PQ, monitored values
x | x | x | x |  | Number of power failures |  | 1 | 0 | 0-0:96.7.21.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600715FF" | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x
x | x | x | x |  | Number of long power failures |  | 1 | 0 | 0-0:96.7.9.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600709FF" | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x
x | x | x | x |  | Time threshold for long power failure |  | 3 | 0 | 0-0:96.7.20.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600714FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  | 180 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,7} | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Duration of last long power failure |  | 3 | 0 | 0-0:96.7.19.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600713FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,7} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Threshold for voltage sag |  | 3 | 0 | 1-0:12.31.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "01000C1F00FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  | 207 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,35} | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Time threshold for voltage sag |  | 3 | 0 | 1-0:12.43.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "01000C2B00FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  | 30 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,7} | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Number of voltage sags in phase L1 |  | 1 | 0 | 1-0:32.32.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100202000FF" | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x
| x |  | x |  | Number of voltage sags in phase L2 |  | 1 | 0 | 1-0:52.32.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100342000FF" | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x
| x |  | x |  | Number of voltage sags in phase L3 |  | 1 | 0 | 1-0:72.32.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100482000FF" | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x
x | x | x | x |  | Duration of last voltage sag in phase L1 |  | 3 | 0 | 1-0:32.33.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100202100FF" | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,7} | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
| x |  | x |  | Duration of last voltage sag in phase L2 |  | 3 | 0 | 1-0:52.33.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100342100FF" | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,7} | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Duration of last voltage sag in phase L3 |  | 3 | 0 | 1-0:72.33.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100482100FF" | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,7} | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
x | x | x | x |  | Magnitude of last voltage sag in phase L1 |  | 3 | 0 | 1-0:32.34.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100202200FF" | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,35} | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
| x |  | x |  | Magnitude of last voltage sag in phase L2 |  | 3 | 0 | 1-0:52.34.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100342200FF" | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,35} | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Magnitude of last voltage sag in phase L3 |  | 3 | 0 | 1-0:72.34.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100482200FF" | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,35} | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
x | x | x | x |  | Threshold for voltage swell |  | 3 | 0 | 1-0:12.35.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "01000C2300FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  | 253 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,35} | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Time threshold for voltage swell |  | 3 | 0 | 1-0:12.44.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "01000C2C00FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  | 30 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,7} | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Number of voltage swells in phase L1 |  | 1 | 0 | 1-0:32.36.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100202400FF" | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x
| x |  | x |  | Number of voltage swells in phase L2 |  | 1 | 0 | 1-0:52.36.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100342400FF" | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x
| x |  | x |  | Number of voltage swells in phase L3 |  | 1 | 0 | 1-0:72.36.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100482400FF" | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x
x | x | x | x |  | Duration of last voltage swell in phase L1 |  | 3 | 0 | 1-0:32.37.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100202500FF" | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,7} | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
| x |  | x |  | Duration of last voltage swell in phase L2 |  | 3 | 0 | 1-0:52.37.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100342500FF" | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,7} | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Duration of last voltage swell in phase L3 |  | 3 | 0 | 1-0:72.37.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100482500FF" | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,7} | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
x | x | x | x |  | Magnitude of last voltage swell in phase L1 |  | 3 | 0 | 1-0:32.38.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100202600FF" | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,35} | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
| x |  | x |  | Magnitude of last voltage swell in phase L2 |  | 3 | 0 | 1-0:52.38.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100342600FF" | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,35} | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Magnitude of last voltage swell in phase L3 |  | 3 | 0 | 1-0:72.38.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100482600FF" | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,35} | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
x | x | x | x |  | Threshold for missing voltage (voltage cut) |  | 3 | 0 | 1-0:12.39.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "01000C2700FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  | 103 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,35} | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Time threshold for voltage cut |  | 3 | 0 | 1-0:12.45.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "01000C2D00FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  | 30 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,7} | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Number of voltage cuts in phase L1 |  | 1 | 0 | 1-0:32.40.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100202800FF" | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x
| x |  | x |  | Number of voltage cuts in phase L2 |  | 1 | 0 | 1-0:52.40.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100342800FF" | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x
| x |  | x |  | Number of voltage cuts in phase L3 |  | 1 | 0 | 1-0:72.40.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100482800FF" | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x
x | x | x | x |  | Duration of last voltage cut in phase L1 |  | 3 | 0 | 1-0:32.41.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100202900FF" | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,7} | -- | Get | -- | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
| x |  | x |  | Duration of last voltage cut in phase L2 |  | 3 | 0 | 1-0:52.41.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100342900FF" | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,7} | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Duration of last voltage cut in phase L3 |  | 3 | 0 | 1-0:72.41.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100482900FF" | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,7} | -- | Get | -- | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
x | x | x | x |  | Power Failure Event Log |  | 7 | 1 | 1-0:99.97.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100636100FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {3,0-0:96.7.19.255,2,0}} | -- | Get | Get | Get | -- | -- | -- | Get | clock;duration of long power failures in any phase
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | asynchronously
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [10..*] | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | Event Object - Power Quality Log |  | 1 | 0 | 0-0:96.11.4.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600B04FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
x | x | x | x
x | x | x | x |  | Power Quality Log |  | 7 | 1 | 0-0:99.98.4.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000636204FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.11.4.255,2,0}} | -- | Get | Get | Get | -- | -- | -- | Get | clock;event code
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | asynchronously
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [100..*] | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | Instantaneous voltage L1 |  | 3 | 0 | 1-0:32.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100200700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {-1,35} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=-1, unit=V resolution: 0.0 V
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Average voltage L1 |  | 3 | 0 | 1-0:32.24.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100201800FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | averaged voltage according to attribute “capture period” of the object “measuring period 3”
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {-1,35} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=-1, unit=V resolution: 0.0 V
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Min voltage L1 |  | 3 | 0 | 1-0:32.23.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100201700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | min voltage in interval defined by attribute “capture period” of the object “measuring period 3”
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {-1,35} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=-1, unit=V resolution: 0.0 V
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Max voltage L1 |  | 3 | 0 | 1-0:32.26.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100201A00FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | max voltage in interval defined by attribute “capture period” of the object “measuring period 3”
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {-1,35} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=-1, unit=V resolution: 0.0 V
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Instantaneous current L1 |  | 3 | 0 | 1-0:31.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "01001F0700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {-2,33} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=-2, unit=A resolution: 0.00 A
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Average current L1 |  | 3 | 0 | 1-0:31.24.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "01001F1800FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | averaged current according to attribute “capture period” of the object “measuring period 3”
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {-2,33} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=-2, unit=A resolution: 0.00 A
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Instantaneous active import power (+P) L1 |  | 3 | 0 | 1-0:21.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100150700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,27} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Instantaneous active export power (-P) L1 |  | 3 | 0 | 1-0:22.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100160700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,27} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Instantaneous reactive import power (+Q) L1 |  | 3 | 0 | 1-0:23.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100170700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,29} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Instantaneous reactive export power (-Q) L1 |  | 3 | 0 | 1-0:24.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100180700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,29} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Instantaneous apparent import power (+S) L1 |  | 3 | 0 | 1-0:29.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "01001D0700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,28} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Instantaneous apparent export power (-S) L1 |  | 3 | 0 | 1-0:30.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "01001E0700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,28} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
| x |  | x |  | Instantaneous voltage L2 |  | 3 | 0 | 1-0:52.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100340700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {-1,35} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=-1, unit=V resolution: 0.0 V
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Average voltage L2 |  | 3 | 0 | 1-0:52.24.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100341800FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | averaged voltage according to attribute “capture period” of the object “measuring period 3”
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {-1,35} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=-1, unit=V resolution: 0.0 V
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Min voltage L2 |  | 3 | 0 | 1-0:52.23.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100341700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | min voltage in interval defined by attribute “capture period” of the object “measuring period 3”
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {-1,35} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=-1, unit=V resolution: 0.0 V
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Max voltage L2 |  | 3 | 0 | 1-0:52.26.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100341A00FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | max voltage in interval defined by attribute “capture period” of the object “measuring period 3”
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {-1,35} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=-1, unit=V resolution: 0.0 V
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Instantaneous current L2 |  | 3 | 0 | 1-0:51.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100330700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {-2,33} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=-2, unit=A resolution: 0.00 A
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Average current L2 |  | 3 | 0 | 1-0:51.24.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100331800FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | averaged current according to attribute “capture period” of the object “measuring period 3”
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {-2,33} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=-2, unit=A resolution: 0.00 A
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Instantaneous active import power (+P) L2 |  | 3 | 0 | 1-0:41.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100290700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,27} | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Instantaneous active export power (-P) L2 |  | 3 | 0 | 1-0:42.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "01002A0700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,27} | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Instantaneous reactive import power (+Q) L2 |  | 3 | 0 | 1-0:43.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "01002B0700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,29} | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Instantaneous reactive export power (-Q) L2 |  | 3 | 0 | 1-0:44.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "01002C0700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,29} | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Instantaneous apparent import power (+S) L2 |  | 3 | 0 | 1-0:49.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100310700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,28} | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Instantaneous apparent export power (-S) L2 |  | 3 | 0 | 1-0:50.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100320700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,28} | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Instantaneous voltage L3 |  | 3 | 0 | 1-0:72.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100480700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {-1,35} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=-1, unit=V resolution: 0.0 V
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Average voltage L3 |  | 3 | 0 | 1-0:72.24.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100481800FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | averaged voltage according to attribute “capture period” of the object “measuring period 3”
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {-1,35} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=-1, unit=V resolution: 0.0 V
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Min voltage L3 |  | 3 | 0 | 1-0:72.23.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100481700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | min voltage in interval defined by attribute “capture period” of the object “measuring period 3”
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {-1,35} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=-1, unit=V resolution: 0.0 V
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Max voltage L3 |  | 3 | 0 | 1-0:72.26.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100481A00FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | max voltage in interval defined by attribute “capture period” of the object “measuring period 3”
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {-1,35} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=-1, unit=V resolution: 0.0 V
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Instantaneous current L3 |  | 3 | 0 | 1-0:71.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100470700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {-2,33} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=-2, unit=A resolution: 0.00 A
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Average current L3 |  | 3 | 0 | 1-0:71.24.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100471800FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | averaged current according to attribute “capture period” of the object “measuring period 3”
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {-2,33} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=-2, unit=A resolution: 0.00 A
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Instantaneous active import power (+P) L3 |  | 3 | 0 | 1-0:61.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "01003D0700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,27} | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Instantaneous active export power (-P) L3 |  | 3 | 0 | 1-0:62.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "01003E0700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,27} | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Instantaneous reactive import power (+Q) L3 |  | 3 | 0 | 1-0:63.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "01003F0700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,29} | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Instantaneous reactive export power (-Q) L3 |  | 3 | 0 | 1-0:64.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100400700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,29} | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Instantaneous apparent import power (+S) L3 |  | 3 | 0 | 1-0:69.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100450700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,28} | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Instantaneous apparent export power (-S) L3 |  | 3 | 0 | 1-0:70.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100460700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,28} | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
x | x | x | x |  | Instantaneous current (sum over all phases) |  | 3 | 0 | 1-0:90.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "01005A0700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | total current (sum of all phases) => algebraic sum of the – unsigned – value of the currents in all phases
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {-2,33} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=0,-1 or-2, unit=A resolution: 0, 0.0 or 0.00 A
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Instantaneous net frequency; any phase |  | 3 | 0 | 1-0:14.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "01000E0700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {-2,44} | -- | Get | Get | Get | -- | -- | -- | Get | scaler=0,-1 or-2, unit=Hz resolution: 0, 0.0 or 0.00 Hz
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Instantaneous active power (¦+P¦+¦-P¦) |  | 3 | 0 | 1-0:15.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "01000F0700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | sum of all phases: ¦QI+QIV¦+¦QII+QIII¦
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,27} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Instantaneous active import power (+P) |  | 3 | 0 | 1-0:1.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100010700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,27} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Instantaneous active export power (-P) |  | 3 | 0 | 1-0:2.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100020700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,27} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Instantaneous reactive import power (+Q) |  | 3 | 0 | 1-0:3.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100030700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,29} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Instantaneous reactive export power (-Q) |  | 3 | 0 | 1-0:4.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100040700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,29} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Instantaneous apparent import power (+S) |  | 3 | 0 | 1-0:9.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100090700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,28} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Instantaneous apparent export power (-S) |  | 3 | 0 | 1-0:10.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "01000A0700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,28} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Instantaneous Power factor import (¦+P/+S¦) |  | 3 | 0 | 1-0:13.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "01000D0700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | Power factor quantities with C = 13, 33, 53, 73 are calculated as PF+ = Active power+ (C = 1, 21, 41, 61) / Apparent power+ (C = 9, 29, 49, 69) This quantity is the power factor in the import direction; it has no sign.
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {-3,255} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Instantaneous Power factor import (¦+P/+S¦) L1 |  | 3 | 0 | 1-0:33.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100210700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | Power factor quantities with C = 13, 33, 53, 73 are calculated as PF+ = Active power+ (C = 1, 21, 41, 61) / Apparent power+ (C = 9, 29, 49, 69) This quantity is the power factor in the import direction; it has no sign.
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {-3,255} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
| x |  | x |  | Instantaneous Power factor import (¦+P/+S¦) L2 |  | 3 | 0 | 1-0:53.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100350700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | Power factor quantities with C = 13, 33, 53, 73 are calculated as PF+ = Active power+ (C = 1, 21, 41, 61) / Apparent power+ (C = 9, 29, 49, 69) This quantity is the power factor in the import direction; it has no sign.
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {-3,255} | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Instantaneous Power factor import (¦+P/+S¦) L3 |  | 3 | 0 | 1-0:73.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100490700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | Power factor quantities with C = 13, 33, 53, 73 are calculated as PF+ = Active power+ (C = 1, 21, 41, 61) / Apparent power+ (C = 9, 29, 49, 69) This quantity is the power factor in the import direction; it has no sign.
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {-3,255} | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
x | x | x | x |  | Instantaneous Power factor export (¦-P/-S¦) |  | 3 | 0 | 1-0:84.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100540700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | Power factor quantities C = 84, 85, 86 and 87 are always calculated as PF- = Active power– (C = 2, 22, 42, 62) / Apparent power- (C = 10, 30, 50, 70). This quantity is the power factor in the export direction; it has no sign.
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {-3,255} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Instantaneous Power factor export (¦-P/-S¦) L1 |  | 3 | 0 | 1-0:85.7.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100550700FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | Power factor quantities C = 84, 85, 86 and 87 are always calculated as PF- = Active power– (C = 2, 22, 42, 62) / Apparent power- (C = 10, 30, 50, 70). This quantity is the power factor in the export direction; it has no sign.
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {-3,255} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
| x |  | x |  | Instantaneous Power factor export (¦-P/-S¦) L2 |  | 3 | 0 | 1-0:86.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100560700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | Power factor quantities C = 84, 85, 86 and 87 are always calculated as PF- = Active power– (C = 2, 22, 42, 62) / Apparent power- (C = 10, 30, 50, 70). This quantity is the power factor in the export direction; it has no sign.
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {-3,255} | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Instantaneous Power factor export (¦-P/-S¦) L3 |  | 3 | 0 | 1-0:87.7.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100570700FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | Power factor quantities C = 84, 85, 86 and 87 are always calculated as PF- = Active power– (C = 2, 22, 42, 62) / Apparent power- (C = 10, 30, 50, 70). This quantity is the power factor in the export direction; it has no sign.
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {-3,255} | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
x | x | x | x |  | Instantaneous Phase Angle (U(L1) to I(L1)) |  | 3 | 0 | 1-0:81.7.40.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100510728FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | Phase Angle from U1 to I1
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,8} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
| x |  | x |  | Instantaneous Phase Angle (U(L2) to I(L2)) |  | 3 | 0 | 1-0:81.7.51.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100510733FF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | Phase Angle from U2 to I2
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,8} | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x |  | x |  | Instantaneous Phase Angle (U(L3) to I(L3)) |  | 3 | 0 | 1-0:81.7.62.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "010051073EFF" | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 2 | value | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | Phase Angle from U3 to I3
| x |  | x | 3 | scaler_unit | scal_unit_type |  |  | {0,8} | -- | Get | Get | Get | -- | -- | -- | Get
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
| x | x | x |  | Measurement Period 3 for Instantaneous values |  | 3 | 0 | 1-0:0.8.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0100000802FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | double_long_unsigned |  |  | 600 | -- | Get | Get | Get, Set | -- | -- | -- | Get, Set | Used with simple average scheme (see IC3, D=23,24,26)
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  | {0,7} | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x | x | x
x | x | x | x |  | Profile status - Power Quality profile |  | 1 | 0 | 0-0:96.10.3.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600A03FF" | -- | Get | Get | Get | Get | -- | -- | Get
x | x | x | x | 2 | status | unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get | bitmask :: {PDN,reserved,CAD,reserved,DST,DNV,CIV,ERR}
x | x | x | x
x |  | x |  |  | Power Quality profile Periodical registering the power quality relevant values |  | 7 | 1 | 1-0:99.14.0.255
x |  | x |  | 1 | logical_name | octet_string[6] |  |  | "0100630E00FF" | -- | Get | Get | Get | Get | -- | -- | Get
x |  | x |  | 2 | buffer | array |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get | selective access per range and entry
x |  | x |  | 3 | capture_objects | array[2..12](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.10.3.255,2,0}, {3,1-0:32.24.0.255,2,0}, {3,1-0:32.23.0.255,2,0}, {3,1-0:32.26.0.255,2,0} } | -- | Get | Get | Get, Set | Get | -- | -- | Get, Set | clock;AMR profile status; average Voltages per phase min Voltages per phase max Voltages per phase
x |  | x |  | 4 | capture_period | double_long_unsigned |  |  | 600 | -- | Get | Get | Get, Set | Get | -- | -- | Get, Set | 1,5,10,15, 60 min, the value is equal to the averaging period of all the captured objects. Further, the averaging periods of the captured objects and the capture_period must be synchronised setting this value to 0 disable the profile recording default 10min
x |  | x |  | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | Get | -- | -- | Get | unsorted (FIFO)
x |  | x |  | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | Get | -- | -- | Get | unsorted
x |  | x |  | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x |  | x |  | 8 | profile_entries | double_long_unsigned |  |  | 1152 | -- | Get | Get | Get | Get | -- | -- | Get | 8 days with 10 min ( min 1152 entries)
x |  | x |  | 1 | reset |  |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res -
x |  | x |  | 2 | capture |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x |  | x
| x |  | x |  | Power Quality profile Periodical registering the power quality relevant values |  | 7 | 1 | 1-0:99.14.0.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0100630E00FF" | -- | Get | Get | Get | Get | -- | -- | Get
| x |  | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get | selective access per range and entry
| x |  | x | 3 | capture_objects | array[2..12](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.10.3.255,2,0}, {3,1-0:32.24.0.255,2,0}, {3,1-0:52.24.0.255,2,0}, {3,1-0:72.24.0.255,2,0}, {3,1-0:32.23.0.255,2,0}, {3,1-0:52.23.0.255,2,0}, {3,1-0:72.23.0.255,2,0}, {3,1-0:32.26.0.255,2,0}, {3,1-0:52.26.0.255,2,0}, {3,1-0:72.26.0.255,2,0}} | -- | Get | Get | Get, Set | Get | -- | -- | Get, Set | clock;AMR profile status; average Voltages per phase min Voltages per phase max Voltages per phase
| x |  | x | 4 | capture_period | double_long_unsigned |  |  | 600 | -- | Get | Get | Get, Set | Get | -- | -- | Get, Set | 1,5,10,15, 60 min, the value is equal to the averaging period of all the captured objects. Further, the averaging periods of the captured objects and the capture_period must be synchronised setting this value to 0 disable the profile recording default 10min
| x |  | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | Get | -- | -- | Get | unsorted (FIFO)
| x |  | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | Get | -- | -- | Get | unsorted
| x |  | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
| x |  | x | 8 | profile_entries | double_long_unsigned |  |  | 1152 | -- | Get | Get | Get | Get | -- | -- | Get | 8 days with 10 min ( min 1152 entries)
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res -
| x |  | x | 2 | capture |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x
x |  | x |  |  | Instantaneous Readout profile Provides snapshot of instantaneous values for readout |  | 7 | 1 | 0-0:21.0.5.255
x |  | x |  | 1 | logical_name | octet_string[6] |  |  | "0000150005FF" | -- | Get | Get | Get | Get | -- | -- | Get
x |  | x |  | 2 | buffer | array |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get | selective access per range and entry
x |  | x |  | 3 | capture_objects | array[0..41](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {3,1-0:32.7.0.255,2,0}, {3,1-0:31.7.0.255,2,0}, …….} | -- | Get | Get | Get, Set | Get | -- | -- | Get, Set | clock; all instantaneous values for SP
x |  | x |  | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get, Set | Get | -- | -- | Get, Set | external trigger by remote
x |  | x |  | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | Get | -- | -- | Get | unsorted (FIFO)
x |  | x |  | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | Get | -- | -- | Get | unsorted
x |  | x |  | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
x |  | x |  | 8 | profile_entries | double_long_unsigned |  |  | 1 | -- | Get | Get | Get | Get | -- | -- | Get | single entry
x |  | x |  | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x |  | x |  | 2 | capture |  |  |  |  | -- | Action | Action | Action | Action | -- | -- | Action
x |  | x
| x |  | x |  | Instantaneous Readout profile Provides snapshot of instantaneous values for readout |  | 7 | 1 | 0-0:21.0.5.255
| x |  | x | 1 | logical_name | octet_string[6] |  |  | "0000150005FF" | -- | Get | Get | Get | Get | -- | -- | Get
| x |  | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get | selective access per range and entry
| x |  | x | 3 | capture_objects | array[0..41](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {3,1-0:32.7.0.255,2,0}, {3,1-0:52.7.0.255,2,0}, {3,1-0:72.7.0.255,2,0}, {3,1-0:31.7.0.255,2,0}, {3,1-0:51.7.0.255,2,0},{3,1-0:71.7.0.255,2,0}, …….} | -- | Get | Get | Get, Set | Get | -- | -- | Get, Set | clock; all instantaneous values for PP
| x |  | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get, Set | Get | -- | -- | Get, Set | external trigger by remote
| x |  | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | Get | -- | -- | Get | unsorted (FIFO)
| x |  | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | Get | -- | -- | Get | unsorted
| x |  | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | Get | -- | -- | Get
| x |  | x | 8 | profile_entries | double_long_unsigned |  |  | 1 | -- | Get | Get | Get | Get | -- | -- | Get | single entry
| x |  | x | 1 | reset |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
| x |  | x | 2 | capture |  |  |  |  | -- | Action | Action | Action | Action | -- | -- | Action
| x |  | x
x | x | x | x |  | Local communication - M-Bus
x | x | x | x |  | M-Bus master port setup 1 |  | 74 | 0 | 0-0:24.6.0.255 | [8 empty] | Wired M-Bus port setup
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000180600FF" | -- | -- | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | comm_speed | enum |  |  | 3 | -- | -- | Get | Get | -- | -- | -- | Get | 3== 2400 bps fix
x | x | x | x
x | x | x | x |  | M-Bus master port setup 2 |  | 74 | 0 | 0-1:24.6.0.255 | [8 empty] | Wireless M-Bus port setup
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0001180600FF" | -- |  |  |  |  | -- | -- | Get
x | x | x | x | 2 | comm_speed | enum |  |  |  | -- |  |  |  |  | -- | -- | Get | (0) 300 bps, (1) 600 bps, (2) 1200 bps, (3) 2400 bps, (4) 4800 bps, (5) 9600 bps, (6) 19200 bps...
x | x | x | x
x | x | x | x |  | M-Bus client channel 1 |  | 72 | 1 | 0-1:24.1.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0001180100FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | mbus_port_reference | octet_string[6] |  |  | 0-0:24.6.0.255 | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute identifies the M-Bus port to be used for this client channel. There are 2 possibilities defined: - wired M-Bus interface => 0-0:24.6.0.255 - wireless M-Bus interface => 0-1:24.6.0.255 Data type: octet_stringd Authorized values: 0-0:24.6.0.255 0-1:24.6.0.255 Default value: 0-0:24.6.0.255
x | x | x | x | 3 | capture_definition | array[0..4] |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute allows a flexible adaptation tor the submeter data elements via the capture_definition attribute. A minimum of up to 4 capture elements must be supported. The sequence of the capture configuration is reflected in the instance count of the M-Bus Value objects Data type: array Authorized values: up to 4 DIF/VIF combintions Default value: empty array
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | Specifies in seconds the readout interval of the connected meters - For wireless M-Bus devices, this value should be set to 0 (externally triggered) - For wired M-Bus devices, the value depends on the usage of the retrieved data Data type: double_long_unsigned Authorized values: 0 = externally triggered 60 (1min) - 2592000 (30days) Default value: 0
x | x | x | x | 5 | primary_address | unsigned |  |  | 0 | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute is only used in combination with the wired M-Bus interface. The Primary address is automatically assigned during the installation process if it was initially set to 0. Setting this attribute to a specific value by the HES is possible if no installation process is required to integrate a M-Bus device. Data type: unsigned Authorized values: 0-250 Default value: 0
x | x | x | x | 6 | identification_number | double_long_unsigned |  |  | 0 | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute represents the Identification Number of the M-Bus Address (part of the M-Bus Data Header) Contains the integer value represented by the 8 BCD digits (not BCD !) Data type: double-long-unsigned Authorized values: no restriction Default value: 0
x | x | x | x | 7 | manufacturer_id | long_unsigned |  |  | 0 | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute represents the Manufacturer identification of the M-Bus Address (part of the M-Bus Data Header) Data type: long-unsigned Authorized values: no restriction Default value: 0
x | x | x | x | 8 | version | unsigned |  |  | 0 | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute represents the Version identification of the M-Bus Address (part of the M-Bus Data Header) Data type: unsigned Authorized values: no restriction Default value: 0
x | x | x | x | 9 | device_type | unsigned |  |  | 0 | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | Represents the Device type identification of the M-Bus Address (part of the M-Bus Data Header) Data type: unsigned Authorized values: no restriction Default value: 0
x | x | x | x | 10 | access_number | unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | This attribute contains the value of the access number, delivered by the M-Bus header Data type: unsigned Default value: 0
x | x | x | x | 11 | status | unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | This attribute contains the value of the status byte, delivered by the M-Bus header Data type: unsigned Default value: 0
x | x | x | x | 12 | alarm | unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | Not supported (always 0)
x | x | x | x | 13 | configuration | long_unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | This attribute contains the value of the configuration field, delivered by the M-Bus header Data type: unsigned Default value: 0
x | x | x | x | 14 | encryption_key_status | enum |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | Provides information on the status of the encryption key. Data type: enum Authorised values: (0) no encryption key, (1) encryption_key set, (2) encryption_key transferred, (3) encryption_key set and transferred, (4) encryption_key in use. Default value: 0
x | x | x | x | 1 | slave_install | unsigned |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 2 | slave_deinstall | unsigned |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 3 | capture | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 4 | reset_alarm | integer |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not supported
x | x | x | x | 5 | synchronize_clock | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 6 | data_send | array |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 7 | set_encryption_key | octet_string |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 8 | transfer_key | octet_string |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus client channel 2 |  | 72 | 1 | 0-2:24.1.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0002180100FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | mbus_port_reference | octet_string[6] |  |  | choice(0-0:24.6.0.255, 0-1:24.6.0.255) | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute identifies the M-Bus port to be used for this client channel. There are 2 possibilities defined: - wired M-Bus interface => 0-0:24.6.0.255 - wireless M-Bus interface => 0-1:24.6.0.255 Data type: octet_stringd Authorized values: 0-0:24.6.0.255 0-1:24.6.0.255 Default value: 0-0:24.6.0.255
x | x | x | x | 3 | capture_definition | array |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute allows a flexible adaptation tor the submeter data elements via the capture_definition attribute. A minimum of up to 4 capture elements must be supported. The sequence of the capture configuration is reflected in the instance count of the M-Bus Value objects Data type: array Authorized values: up to 4 DIF/VIF combintions Default value: empty array
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | Specifies in seconds the readout interval of the connected meters - For wireless M-Bus devices, this value should be set to 0 (externally triggered) - For wired M-Bus devices, the value depends on the usage of the retrieved data Data type: double_long_unsigned Authorized values: 0 = externally triggered 60 (1min) - 2592000 (30days) Default value: 0
x | x | x | x | 5 | primary_address | unsigned |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute is only used in combination with the wired M-Bus interface. The Primary address is automatically assigned during the installation process if it was initially set to 0. Setting this attribute to a specific value by the HES is possible if no installation process is required to integrate a M-Bus device. Data type: unsigned Authorized values: 0-250 Default value: 0
x | x | x | x | 6 | identification_number | double_long_unsigned |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute represents the Identification Number of the M-Bus Address (part of the M-Bus Data Header) Contains the integer value represented by the 8 BCD digits (not BCD !) Data type: double-long-unsigned Authorized values: no restriction Default value: 0
x | x | x | x | 7 | manufacturer_id | long_unsigned |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute represents the Manufacturer identification of the M-Bus Address (part of the M-Bus Data Header) Data type: long-unsigned Authorized values: no restriction Default value: 0
x | x | x | x | 8 | version | unsigned |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute represents the Version identification of the M-Bus Address (part of the M-Bus Data Header) Data type: unsigned Authorized values: no restriction Default value: 0
x | x | x | x | 9 | device_type | unsigned |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | Represents the Device type identification of the M-Bus Address (part of the M-Bus Data Header) Data type: unsigned Authorized values: no restriction Default value: 0
x | x | x | x | 10 | access_number | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | This attribute contains the value of the access number, delivered by the M-Bus header Data type: unsigned Default value: 0
x | x | x | x | 11 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | This attribute contains the value of the status byte, delivered by the M-Bus header Data type: unsigned Default value: 0
x | x | x | x | 12 | alarm | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | Not supported (always 0)
x | x | x | x | 13 | configuration | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | This attribute contains the value of the configuration field, delivered by the M-Bus header Data type: unsigned Default value: 0
x | x | x | x | 14 | encryption_key_status | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | Provides information on the status of the encryption key. Data type: enum Authorised values: (0) no encryption key, (1) encryption_key set, (2) encryption_key transferred, (3) encryption_key set and transferred, (4) encryption_key in use. Default value: 0
x | x | x | x | 1 | slave_install | unsigned |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 2 | slave_deinstall | unsigned |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 3 | capture | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 4 | reset_alarm | integer |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not supported
x | x | x | x | 5 | synchronize_clock | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 6 | data_send | array |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 7 | set_encryption_key | octet_string |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 8 | transfer_key | octet_string |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus client channel 3 |  | 72 | 1 | 0-3:24.1.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0003180100FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | mbus_port_reference | octet_string[6] |  |  | choice(0-0:24.6.0.255, 0-1:24.6.0.255) | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute identifies the M-Bus port to be used for this client channel. There are 2 possibilities defined: - wired M-Bus interface => 0-0:24.6.0.255 - wireless M-Bus interface => 0-1:24.6.0.255 Data type: octet_stringd Authorized values: 0-0:24.6.0.255 0-1:24.6.0.255 Default value: 0-0:24.6.0.255
x | x | x | x | 3 | capture_definition | array |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute allows a flexible adaptation tor the submeter data elements via the capture_definition attribute. A minimum of up to 4 capture elements must be supported. The sequence of the capture configuration is reflected in the instance count of the M-Bus Value objects Data type: array Authorized values: up to 4 DIF/VIF combintions Default value: empty array
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | Specifies in seconds the readout interval of the connected meters - For wireless M-Bus devices, this value should be set to 0 (externally triggered) - For wired M-Bus devices, the value depends on the usage of the retrieved data Data type: double_long_unsigned Authorized values: 0 = externally triggered 60 (1min) - 2592000 (30days) Default value: 0
x | x | x | x | 5 | primary_address | unsigned |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute is only used in combination with the wired M-Bus interface. The Primary address is automatically assigned during the installation process if it was initially set to 0. Setting this attribute to a specific value by the HES is possible if no installation process is required to integrate a M-Bus device. Data type: unsigned Authorized values: 0-250 Default value: 0
x | x | x | x | 6 | identification_number | double_long_unsigned |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute represents the Identification Number of the M-Bus Address (part of the M-Bus Data Header) Contains the integer value represented by the 8 BCD digits (not BCD !) Data type: double-long-unsigned Authorized values: no restriction Default value: 0
x | x | x | x | 7 | manufacturer_id | long_unsigned |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute represents the Manufacturer identification of the M-Bus Address (part of the M-Bus Data Header) Data type: long-unsigned Authorized values: no restriction Default value: 0
x | x | x | x | 8 | version | unsigned |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute represents the Version identification of the M-Bus Address (part of the M-Bus Data Header) Data type: unsigned Authorized values: no restriction Default value: 0
x | x | x | x | 9 | device_type | unsigned |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | Represents the Device type identification of the M-Bus Address (part of the M-Bus Data Header) Data type: unsigned Authorized values: no restriction Default value: 0
x | x | x | x | 10 | access_number | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | This attribute contains the value of the access number, delivered by the M-Bus header Data type: unsigned Default value: 0
x | x | x | x | 11 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | This attribute contains the value of the status byte, delivered by the M-Bus header Data type: unsigned Default value: 0
x | x | x | x | 12 | alarm | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | Not supported (always 0)
x | x | x | x | 13 | configuration | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | This attribute contains the value of the configuration field, delivered by the M-Bus header Data type: unsigned Default value: 0
x | x | x | x | 14 | encryption_key_status | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | Provides information on the status of the encryption key. Data type: enum Authorised values: (0) no encryption key, (1) encryption_key set, (2) encryption_key transferred, (3) encryption_key set and transferred, (4) encryption_key in use. Default value: 0
x | x | x | x | 1 | slave_install | unsigned |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 2 | slave_deinstall | unsigned |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 3 | capture | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 4 | reset_alarm | integer |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not supported
x | x | x | x | 5 | synchronize_clock | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 6 | data_send | array |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 7 | set_encryption_key | octet_string |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 8 | transfer_key | octet_string |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus client channel 4 |  | 72 | 1 | 0-4:24.1.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0004180100FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | mbus_port_reference | octet_string[6] |  |  | choice(0-0:24.6.0.255, 0-1:24.6.0.255) | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute identifies the M-Bus port to be used for this client channel. There are 2 possibilities defined: - wired M-Bus interface => 0-0:24.6.0.255 - wireless M-Bus interface => 0-1:24.6.0.255 Data type: octet_stringd Authorized values: 0-0:24.6.0.255 0-1:24.6.0.255 Default value: 0-0:24.6.0.255
x | x | x | x | 3 | capture_definition | array |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute allows a flexible adaptation tor the submeter data elements via the capture_definition attribute. A minimum of up to 4 capture elements must be supported. The sequence of the capture configuration is reflected in the instance count of the M-Bus Value objects Data type: array Authorized values: up to 4 DIF/VIF combintions Default value: empty array
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | Specifies in seconds the readout interval of the connected meters - For wireless M-Bus devices, this value should be set to 0 (externally triggered) - For wired M-Bus devices, the value depends on the usage of the retrieved data Data type: double_long_unsigned Authorized values: 0 = externally triggered 60 (1min) - 2592000 (30days) Default value: 0
x | x | x | x | 5 | primary_address | unsigned |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute is only used in combination with the wired M-Bus interface. The Primary address is automatically assigned during the installation process if it was initially set to 0. Setting this attribute to a specific value by the HES is possible if no installation process is required to integrate a M-Bus device. Data type: unsigned Authorized values: 0-250 Default value: 0
x | x | x | x | 6 | identification_number | double_long_unsigned |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute represents the Identification Number of the M-Bus Address (part of the M-Bus Data Header) Contains the integer value represented by the 8 BCD digits (not BCD !) Data type: double-long-unsigned Authorized values: no restriction Default value: 0
x | x | x | x | 7 | manufacturer_id | long_unsigned |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute represents the Manufacturer identification of the M-Bus Address (part of the M-Bus Data Header) Data type: long-unsigned Authorized values: no restriction Default value: 0
x | x | x | x | 8 | version | unsigned |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | This attribute represents the Version identification of the M-Bus Address (part of the M-Bus Data Header) Data type: unsigned Authorized values: no restriction Default value: 0
x | x | x | x | 9 | device_type | unsigned |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | Represents the Device type identification of the M-Bus Address (part of the M-Bus Data Header) Data type: unsigned Authorized values: no restriction Default value: 0
x | x | x | x | 10 | access_number | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | This attribute contains the value of the access number, delivered by the M-Bus header Data type: unsigned Default value: 0
x | x | x | x | 11 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | This attribute contains the value of the status byte, delivered by the M-Bus header Data type: unsigned Default value: 0
x | x | x | x | 12 | alarm | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | Not supported (always 0)
x | x | x | x | 13 | configuration | long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | This attribute contains the value of the configuration field, delivered by the M-Bus header Data type: unsigned Default value: 0
x | x | x | x | 14 | encryption_key_status | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | Provides information on the status of the encryption key. Data type: enum Authorised values: (0) no encryption key, (1) encryption_key set, (2) encryption_key transferred, (3) encryption_key set and transferred, (4) encryption_key in use. Default value: 0
x | x | x | x | 1 | slave_install | unsigned |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 2 | slave_deinstall | unsigned |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 3 | capture | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 4 | reset_alarm | integer |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Not supported
x | x | x | x | 5 | synchronize_clock | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 6 | data_send | array |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 7 | set_encryption_key | octet_string |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 8 | transfer_key | octet_string |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Value channel 1, instance 1 |  | 4 | 0 | 0-1:24.2.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0001180201FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | choice(double_long_unsigned,octet_string) |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | time of last successful readout; format same as clock.time
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Value channel 1, instance 2 |  | 4 | 0 | 0-1:24.2.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0001180202FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | choice(double_long_unsigned,octet_string) |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | time of last successful readout; format same as clock.time
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Value channel 1, instance 3 |  | 4 | 0 | 0-1:24.2.3.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0001180203FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | choice(double_long_unsigned,octet_string) |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | time of last successful readout; format same as clock.time
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Value channel 1, instance 4 |  | 4 | 0 | 0-1:24.2.4.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0001180204FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | choice(double_long_unsigned,octet_string) |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | time of last successful readout; format same as clock.time
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Value channel 2, instance 1 |  | 4 | 0 | 0-2:24.2.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0002180201FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | choice(double_long_unsigned,octet_string) |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | time of last successful readout; format same as clock.time
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Value channel 2, instance 2 |  | 4 | 0 | 0-2:24.2.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0002180202FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | choice(double_long_unsigned,octet_string) |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | time of last successful readout; format same as clock.time
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Value channel 2, instance 3 |  | 4 | 0 | 0-2:24.2.3.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0002180203FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | choice(double_long_unsigned,octet_string) |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | time of last successful readout; format same as clock.time
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Value channel 2, instance 4 |  | 4 | 0 | 0-2:24.2.4.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0002180204FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | choice(double_long_unsigned,octet_string) |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | time of last successful readout; format same as clock.time
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Value channel 3, instance 1 |  | 4 | 0 | 0-3:24.2.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0003180201FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | choice(double_long_unsigned,octet_string) |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | time of last successful readout; format same as clock.time
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Value channel 3, instance 2 |  | 4 | 0 | 0-3:24.2.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0003180202FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | choice(double_long_unsigned,octet_string) |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | time of last successful readout; format same as clock.time
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Value channel 3, instance 3 |  | 4 | 0 | 0-3:24.2.3.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0003180203FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | choice(double_long_unsigned,octet_string) |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | time of last successful readout; format same as clock.time
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Value channel 3, instance 4 |  | 4 | 0 | 0-3:24.2.4.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0003180204FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | choice(double_long_unsigned,octet_string) |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | time of last successful readout; format same as clock.time
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Value channel 4, instance 1 |  | 4 | 0 | 0-4:24.2.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0004180201FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | choice(double_long_unsigned,octet_string) |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | time of last successful readout; format same as clock.time
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Value channel 4, instance 2 |  | 4 | 0 | 0-4:24.2.2.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0004180202FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | choice(double_long_unsigned,octet_string) |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | time of last successful readout; format same as clock.time
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Value channel 4, instance 3 |  | 4 | 0 | 0-4:24.2.3.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0004180203FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | choice(double_long_unsigned,octet_string) |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | time of last successful readout; format same as clock.time
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Value channel 4, instance 4 |  | 4 | 0 | 0-4:24.2.4.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0004180204FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | choice(double_long_unsigned,octet_string) |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | scaler_unit | scal_unit_type |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 5 | capture_time | octet_string |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | time of last successful readout; format same as clock.time
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Device ID 1 channel 1 |  | 1 | 0 | 0-1:96.1.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0001600100FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | octet_string[0..48] |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | This attribute represents the Fabrication Number of the M-Bus Device. It contains the ASCII encoded value of the delivered fabrication number. The length of the octet string matches the length of the fabrication number. Data type: Octet_String Default value: empty
x | x | x | x
x | x | x | x |  | M-Bus Device ID 1 channel 2 |  | 1 | 0 | 0-2:96.1.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0002600100FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | octet_string[0..48] |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | This attribute represents the Fabrication Number of the M-Bus Device. It contains the ASCII encoded value of the delivered fabrication number. The length of the octet string matches the length of the fabrication number. Data type: Octet_String Default value: empty
x | x | x | x
x | x | x | x |  | M-Bus Device ID 1 channel 3 |  | 1 | 0 | 0-3:96.1.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0003600100FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | octet_string[0..48] |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | This attribute represents the Fabrication Number of the M-Bus Device. It contains the ASCII encoded value of the delivered fabrication number. The length of the octet string matches the length of the fabrication number. Data type: Octet_String Default value: empty
x | x | x | x
x | x | x | x |  | M-Bus Device ID 1 channel 4 |  | 1 | 0 | 0-4:96.1.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0004600100FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | octet_string[0..48] |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | This attribute represents the Fabrication Number of the M-Bus Device. It contains the ASCII encoded value of the delivered fabrication number. The length of the octet string matches the length of the fabrication number. Data type: Octet_String Default value: empty
x | x | x | x
x | x | x | x |  | M-Bus Device ID 2 channel 1 |  | 1 | 0 | 0-1:96.1.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0001600101FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | octet_string[0..48] |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | This attribute represents the Application Layer Address of the M-Bus Device. It contains the ASCII encoded value of the delivered Application Layer Address. The length of the octet string matches the length of the Application Layer Address. Data type: Octet_String Default value: empty
x | x | x | x
x | x | x | x |  | M-Bus Device ID 2 channel 2 |  | 1 | 0 | 0-2:96.1.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0002600101FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | octet_string[0..48] |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | This attribute represents the Application Layer Address of the M-Bus Device. It contains the ASCII encoded value of the delivered Application Layer Address. The length of the octet string matches the length of the Application Layer Address. Data type: Octet_String Default value: empty
x | x | x | x
x | x | x | x |  | M-Bus Device ID 2 channel 3 |  | 1 | 0 | 0-3:96.1.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0003600101FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | octet_string[0..48] |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | This attribute represents the Application Layer Address of the M-Bus Device. It contains the ASCII encoded value of the delivered Application Layer Address. The length of the octet string matches the length of the Application Layer Address. Data type: Octet_String Default value: empty
x | x | x | x
x | x | x | x |  | M-Bus Device ID 2 channel 4 |  | 1 | 0 | 0-4:96.1.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0004600101FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | octet_string[0..48] |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | This attribute represents the Application Layer Address of the M-Bus Device. It contains the ASCII encoded value of the delivered Application Layer Address. The length of the octet string matches the length of the Application Layer Address. Data type: Octet_String Default value: empty
x | x | x | x
x | x | x | x |  | Profile status for M-Bus Master Load profile 1 |  | 1 | 0 | 0-1:96.10.3.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0001600A03FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x
x | x | x | x |  | Profile status for M-Bus Master Load profile 2 |  | 1 | 0 | 0-2:96.10.3.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0002600A03FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x
x | x | x | x |  | Profile status for M-Bus Master Load profile 3 |  | 1 | 0 | 0-3:96.10.3.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0003600A03FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x
x | x | x | x |  | Profile status for M-Bus Master Load profile 4 |  | 1 | 0 | 0-4:96.10.3.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0004600A03FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | status | unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x
x | x | x | x |  | M-Bus Master Load profile for channel 1 |  | 7 | 1 | 0-1:24.3.0.255 | [8 empty] | Hourly interval readings of M-Bus devices
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0001180300FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2..*](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1, 0-1:96.10.3.255,2,0}, {4, 0-1:24.2.1.255,2,0}, {4, 0-1:24.2.2.255,2,0}, {4, 0-1:24.2.3.255,2,0}, {4, 0-1:24.2.4.255,2,0}} | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | clock;AMR status; M-Bus Master value object;
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 3600 | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | every hour
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [240..*] | -- | Get | Get | Get | -- | -- | -- | Get | ≥10 days
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Master Load profile for channel 2 |  | 7 | 1 | 0-2:24.3.0.255 | [8 empty] | Hourly interval readings of M-Bus devices
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0002180300FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2..*](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1, 0-2:96.10.3.255,2,0}, {4, 0-2:24.2.1.255,2,0}, {4, 0-2:24.2.2.255,2,0}, {4, 0-2:24.2.3.255,2,0}, {4, 0-2:24.2.4.255,2,0}} | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | clock;AMR status; M-Bus Master value object;
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 3600 | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | every hour
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [240..*] | -- | Get | Get | Get | -- | -- | -- | Get | ≥10 days, optional set to restrict maximum capacity according to national laws
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Master Load profile for channel 3 |  | 7 | 1 | 0-3:24.3.0.255 | [8 empty] | Hourly interval readings of M-Bus devices
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0003180300FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2..*](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1, 0-3:96.10.3.255,2,0}, {4, 0-3:24.2.1.255,2,0}, {4, 0-3:24.2.2.255,2,0}, {4, 0-3:24.2.3.255,2,0}, {4, 0-3:24.2.4.255,2,0}} | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | clock;AMR status; M-Bus Master value object;
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 3600 | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | every hour
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [240..*] | -- | Get | Get | Get | -- | -- | -- | Get | ≥10 days, optional set to restrict maximum capacity according to national laws
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Master Load profile for channel 4 |  | 7 | 1 | 0-4:24.3.0.255 | [8 empty] | Hourly interval readings of M-Bus devices
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0004180300FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2..*](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1, 0-4:96.10.3.255,2,0}, {4, 0-4:24.2.1.255,2,0}, {4, 0-4:24.2.2.255,2,0}, {4, 0-4:24.2.3.255,2,0}, {4, 0-4:24.2.4.255,2,0}} | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | clock;AMR status; M-Bus Master value object;
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 3600 | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set | every hour
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [240..*] | -- | Get | Get | Get | -- | -- | -- | Get | ≥10 days, optional set to restrict maximum capacity according to national laws
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Master Disconnect control object 1 |  | 70 | 0 | 0-1:24.4.0.255 | [8 empty] | Controls the opening and closing of an M-Bus disconnector (e.g. gas valve)
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0001180400FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | output_state | boolean |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | control_state | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | control_mode | enum |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 1 | remote_disconnect | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 2 | remote_connect | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Master Disconnect control object 2 |  | 70 | 0 | 0-2:24.4.0.255 | [8 empty] | Controls the opening and closing of an M-Bus disconnector (e.g. gas valve)
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0002180400FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | output_state | boolean |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | control_state | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | control_mode | enum |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 1 | remote_disconnect | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 2 | remote_connect | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Master Disconnect control object 3 |  | 70 | 0 | 0-3:24.4.0.255 | [8 empty] | Controls the opening and closing of an M-Bus disconnector (e.g. gas valve)
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0003180400FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | output_state | boolean |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | control_state | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | control_mode | enum |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 1 | remote_disconnect | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 2 | remote_connect | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Master Disconnect control object 4 |  | 70 | 0 | 0-4:24.4.0.255 | [8 empty] | Controls the opening and closing of an M-Bus disconnector (e.g. gas valve)
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0004180400FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | output_state | boolean |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | control_state | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | control_mode | enum |  |  |  | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 1 | remote_disconnect | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x | 2 | remote_connect | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Disconnect control scheduler |  | 22 | 0 | 0-1:15.0.1.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00010F0001FF" | -- | -- | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | executed_script | script22 |  |  | {0-1:10.0.106.255, [1..16]} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 3 | type | enum |  |  | 1 | -- | -- | Get | Get | -- | -- | -- | Get | 1 is mandatory
x | x | x | x | 4 | execution_time | array[0..1](execution_time_date) |  |  | {} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | dedicated timepoint for connection or disconnection
x | x | x | x
x | x | x | x |  | M-Bus Disconnector script table |  | 9 | 0 | 0-1:10.0.106.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00010A006AFF" | -- | -- | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | scripts | array[16](script9) |  |  | { {1,{{1,70, 0-1:24.4.0.255,3,2}}}, {2,{{1,70, 0-1:24.4.0.255,3,1}}}, {3,{{1,70, 0-2:24.4.0.255,3,2}}}, {4,{{1,70, 0-2:24.4.0.255,3,1}}}, {5,{{1,70, 0-3:24.4.0.255,3,2}}}, {6,{{1,70, 0-3:24.4.0.255,3,1}}}, {7,{{1,70, 0-4:24.4.0.255,3,2}}}, {8,{{1,70, 0-4:24.4.0.255,3,1}}}, {9,{{2,70, 0-1:24.4.0.255,1,0}}}, {10,{{2,70, 0-1:24.4.0.255,2,0}}}, {11,{{2,70, 0-2:24.4.0.255,1,0}}}, {12,{{2,70, 0-2:24.4.0.255,2,0}}}, {13,{{2,70, 0-3:24.4.0.255,1,0}}}, {14,{{2,70, 0-3:24.4.0.255,2,0}}}, {15,{{2,70, 0-4:24.4.0.255,1,0}}}, {16,{{2,70, 0-4:24.4.0.255,2,0}}} } | -- | -- | Get | Get | -- | -- | -- | Get | local and remote connect and disconnect methods of the M-Bus disconnector objects, see E disconnector script table for further details
x | x | x | x | 1 | execute | long_unsigned |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | Executes the script specified in parameter data. If data matches one of the script_identifiers in the script table, then the corresponding action_specification is executed. No direct method call possible via remote communication
x | x | x | x
x | x | x | x |  | Event Objects - M-Bus Master Control logs 1 |  | 1 | 0 | 0-1:96.11.4.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0001600B04FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
x | x | x | x
x | x | x | x |  | Event Objects - M-Bus Master Control logs 2 |  | 1 | 0 | 0-2:96.11.4.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0002600B04FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
x | x | x | x
x | x | x | x |  | Event Objects - M-Bus Master Control logs 3 |  | 1 | 0 | 0-3:96.11.4.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0003600B04FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
x | x | x | x
x | x | x | x |  | Event Objects - M-Bus Master Control logs 4 |  | 1 | 0 | 0-4:96.11.4.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0004600B04FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
x | x | x | x
x | x | x | x |  | M-Bus Master Control log object 1 |  | 7 | 1 | 0-1:24.5.0.255 | [8 empty] | Changes of the states related to the disconnect control are recorded (open, close)
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0001180500FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1, 0-1:96.11.4.255, 2, 0}} | -- | Get | Get | Get | -- | -- | -- | Get | clock;control event code
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | asynchronously
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [10..*] | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Master Control log object 2 |  | 7 | 1 | 0-2:24.5.0.255 | [8 empty] | Changes of the states related to the disconnect control are recorded (open, close)
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0002180500FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1, 0-2:96.11.4.255, 2, 0}} | -- | Get | Get | Get | -- | -- | -- | Get | clock;control event code
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | asynchronously
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [10..*] | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Master Control log object 3 |  | 7 | 1 | 0-3:24.5.0.255 | [8 empty] | Changes of the states related to the disconnect control are recorded (open, close)
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0003180500FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1, 0-3:96.11.4.255, 2, 0}} | -- | Get | Get | Get | -- | -- | -- | Get | clock;control event code
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | asynchronously
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [10..*] | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | M-Bus Master Control log object 4 |  | 7 | 1 | 0-4:24.5.0.255 | [8 empty] | Changes of the states related to the disconnect control are recorded (open, close)
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0004180500FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1, 0-4:96.11.4.255, 2, 0}} | -- | Get | Get | Get | -- | -- | -- | Get | clock;control event code
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | asynchronously
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [10..*] | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | Event Object - M-Bus Event Log |  | 1 | 0 | 0-0:96.11.3.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600B03FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | enum |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | event number (0 to 255); at first power up or if no events were yet generated the value should return 255
x | x | x | x
x | x | x | x |  | M-Bus Event Log |  | 7 | 1 | 0-0:99.98.3.255 | [8 empty] | Event log containing errors and alarms related to all M-Bus devices
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000636203FF" | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get | selective access per range and entry
x | x | x | x | 3 | capture_objects | array[2](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1, 0-0:96.11.3.255, 2, 0}} | -- | Get | Get | Get | -- | -- | -- | Get | clock;event code
x | x | x | x | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | Get | Get | Get | -- | -- | -- | Get | asynchronously
x | x | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
x | x | x | x | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | Get | Get | Get | -- | -- | -- | Get | unsorted
x | x | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 8 | profile_entries | double_long_unsigned |  |  | [100..*] | -- | Get | Get | Get | -- | -- | -- | Get
x | x | x | x | 1 | reset |  |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action Req S, Res -
x | x | x | x
x | x | x | x |  | Local communication - IEC/HDLC Optical port
x | x | x | x |  | IEC HDLC setup - HDLC Optical port |  | 23 | 1 | 0-0:22.0.0.255 | [8 empty] | Mandatory HDLC on Optical port.
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000160000FF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | comm_speed | enum |  |  | 5 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 3 | window_size_transmit | unsigned |  |  | 1 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 4 | window_size_receive | unsigned |  |  | 1 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x | 5 | max_info_field_lenght_transmit | long_unsigned |  |  | 128 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | The maximum information field length that a device can transmit. During logon, a smaller value can be negotiated. Data type: long-unsigned Authorized value: 32 to 1227 Max value defined to support server-max-transmit-pdu-size (1224 bytes) + the HDLC profile LLC header (3 bytes) Default value: 128
x | x | x | x | 6 | max_info_field_lenght_receive | long_unsigned |  |  | 128 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | The maximum information field length that a device can reveice. During logon, a smaller value can be negotiated. Data type: long-unsigned Authorized value: 32 to 1227 Max value defined to support server-max-receive-pdu-size (1224 bytes) + the HDLC profile LLC header (3 bytes) Default value: 128
x | x | x | x | 7 | inter_octet_time_out | long_unsigned |  |  | 25 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | Defines the time, expressed in milliseconds, over which, when no character is received from the primary station, the device will treat the already received data as a complete frame. Data type: long-unsigned Authorized value: 20 to 6000 Default value: 25
x | x | x | x | 8 | inactivity_time_out | long_unsigned |  |  | 120 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | Defines the time, expressed in seconds over which, when no frame is received from the primary station, the device will process a disconnection. Data type: long-unsigned Authorized value: 0 to 65535 When this value is set to 0, this means that the inactivity_time_out is not operational. Default value: 120
x | x | x | x | 9 | device_address | long_unsigned |  |  | 17 | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set
x | x | x | x
x | x | x | x |  | Optical port temp disable |  | 1 | 0 | 0-0:94.43.140.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00005E2B8CFF" | -- | -- | -- | -- | -- | -- | -- | Get
x | x | x | x | 2 | value | long_unsigned |  |  | 0 | -- | -- | -- | -- | -- | -- | -- | Get, Set Req S, Res - | Countdown value in seconds for the temporary disabling of the optical HDLC interface The value initially set to this attribute defines the time disabling time in seconds. The interface is automatically enabled when the value reaches 0. Setting this value to 65535 prevents the countdown of the register, keeping the optical interface permanently disabled Authorized value: 0 to 65535 Default value: 0
x | x | x | x
x | x | x | x |  | Optical port lockout |  | 1 | 0 | 0-0:94.43.141.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00005E2B8DFF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | value | value ::= structure { failed_association_attempts: unsigned lockout_period: long_unsigned } |  |  | {0;0} | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set Req S, Res - | Client_Lockout This object allows the configuration of the lockout parameters failed_association_attempts: Defines the number of failed association attempts before the activation of the lockout period. A value of 0 disables the feature Data type: unsigned Authorised values: 0-255 Default: 0 lockout_period: Defines the lockout period length in number of seconds. Data type: long_unsigned Authorised values: 0-65535 Default: 0
x | x | x | x
x | x | x | x |  | Abstract objects - TCP/IP profile setup
x | x |  |  |  | TCP-UDP setup |  | 41 | 0 | 0-0:25.0.0.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "0000190000FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | TCP-UDP_port | long_unsigned |  |  | 61616 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | Holds the TCP-UDP port number on which the physical device is listening for the DLMS/COSEM application. Data type: UNSIGNED16 Authorized value: 0 to 65535 Default value: 61616
x | x |  |  | 3 | IP_reference | octet_string[6] |  |  | 0-0:25.7.0.255 | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 4 | MSS | long_unsigned |  |  | 1280 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set
x | x |  |  | 5 | nb_of_sim_conn | unsigned |  |  | 1 | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 6 | inactivity_time_out | long_unsigned |  |  | 180 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set
x | x
x | x |  |  |  | IPv6 setup |  | 48 | 0 | 0-0:25.7.0.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "0000190700FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | DL_reference | octet_string[6] |  |  | 0-0:25.2.0.255 | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 3 | address_config_mode | enum |  |  | 3 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | This attribute defines the IPv6 configuration mode. In AUTO_CONFIGURATION mode, exclusive use of link-local and local scope multicast addresses is forced. All attempts aiming to set up a different IP configuration are ignored (such as Router Advertisement messages). In NDP mode, extended range addresses such as ULA and larger scope multicast addresses are used. In this configuration, link-local and local scope muticast addresses may be used alternatively. Data type: ENUMERATED Authorized value: 0 AUTO_CONFIGURATION 3 NDP (Neighbour Discovery) Default value: 3
x | x |  |  | 4 | unicast_IPv6_addresses | array[0..2](IPv6_address) |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | This attribute provides a link-local and optionally an ULA IPv6 address that has been provisioned to the device as defined in the G3 PLC metering profile. In case of PLC G3 profile, only one link local IPv6 address is allocated to the device.
x | x |  |  | 5 | multicast_IPv6_addresses | array[1..16](IPv6_address) |  |  | { 0xFF02 0000 0000 0000 0000 0000 0000 0001; } | -- | -- | Get | Get | -- | -- | Get | Get | When a new multicast IPv6 address is defined, a new group_address shall be added to the adp_group_table attribute, located in the PLCG3AdaptationLayer6LoWPANSetup object. The mapping between the multicast IPv6 address and the corresponding adp address is done according to RFC 4944, chapter 9. In any case, the default element of the multicast_IPv6_addresses attribute shall never be deleted. Default value: 1 entry with Group_address = 0xFF02 0000 0000 0000 0000 0000 0000 0001
x | x |  |  | 6 | gateway_IPv6_address | array[0..*](IPv6_address) |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | not used
x | x |  |  | 7 | primary_DNS_address | IPv6_address |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | not used
x | x |  |  | 8 | secondary_DNS_address | IPv6_address |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | not used
x | x |  |  | 9 | traffic_class | unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set
x | x |  |  | 10 | neighbor_discovery_setup | array[0..1](neighbour_discovery_setup_element) |  |  | {{3,10000,0}} | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | SEQUENCE { RS_max_retry RS_retry_wait_time RA_send_period } RS_max_retry This parameter defines the maximum number of RS retries. Data type: UNSIGNED8 Authorized value: 0 to 255 Default value: 3 RS_retry_wait_time This parameter defines the waiting time between two router solicitation retries in milliseconds. Data type: UNSIGNED16 Authorized value: 1000 to 65535 Default value: 10000 RA_send_period This parameter defines the router advertisement message transmission period in seconds. However this parameter is not used since meters shall not send router advertisement messages. Data type: UNSIGNED32 Authorized value : 0 – 4 294 967 295 Default value: 0
x | x |  |  | 1 | add_IPv6_address | IPv6_address_entry |  |  |  | -- | -- | Action | Action | -- | -- | Action | Action | This method allows the client system to subscribe the server to a new multicast IPv6 address. When a new multicast IPv6 address is defined, a new group_address shall be added to the adp_group_table attribute, located in the PLCG3AdaptationLayer6LoWPANSetup object. The mapping between the multicast IPv6 address and the corresponding adp address is done according to RFC 4944, chapter 9. In any case, the default element of the multicast_IPv6_addresses attribute shall never be deleted. SEQUENCE // 2 elements { IPv6_address_type IPv6_address } IPv6_address_type Data type: ENUMERATED Authorized value: 1: multicast IPv6_address Data type: OCTETSTRING
x | x |  |  | 2 | remove_IPv6_address | IPv6_address_entry |  |  |  | -- | -- | Action | Action | -- | -- | Action | Action | This method allows the client system to unsubscribe the server to a multicast IPv6 address. In any case, the default element of the multicast_IPv6_addresses attribute shall never be deleted. SEQUENCE // 2 elements { IPv6_address_type IPv6_address } IPv6_address_type Data type: ENUMERATED Authorized value: 1: multicast IPv6_address Data type: OCTETSTRING
x | x
|  | x | x |  | IPv4 IPv6 selection |  | 1 | 0 | 0-0:96.5.0.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600500FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | enum |  |  | 3 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | The internet protocol mode is configured and managed via the COSEM object [IPv4 IPv6 selection]. Value IPv4 = 1, IPv6 = 2, IPv4v6 = 3 (default)
|  | x | x
|  | x | x |  | TCP-UDP setup |  | 41 | 0 | 0-0:25.0.0.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000190000FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | TCP-UDP_port | long_unsigned |  |  | 4059 | -- | -- | Get | Get | -- | -- | -- | Get | Holds the TCP-UDP port number on which the physical device is listening for the DLMS/COSEM application. Data type: UNSIGNED16 Authorized value: 0 to 65535 Default value: 4059
|  | x | x | 3 | IP_reference | octet_string[6] |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 4 | MSS | long_unsigned |  |  | 576 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set
|  | x | x | 5 | nb_of_sim_conn | unsigned |  |  | 1 | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 6 | inactivity_time_out | long_unsigned |  |  | 300 | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x
|  | x | x |  | IPv4 setup |  | 42 | 0 | 0-0:25.1.0.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000190100FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | DL_reference | octet_string[6] |  |  | 0-0:25.3.0.255 | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 3 | IP_address | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 4 | multicast_IP_address | array[0..*] |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 5 | IP_options | array[0..*] |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 6 | subnet_mask | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 7 | gateway_IP_address | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 8 | use_DHCP_flag | boolean |  |  | TRUE | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set
|  | x | x | 9 | primary_DNS_address | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 10 | secondary_DNS_address | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 1 | add_mc_IP_address | double_long_unsigned |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
|  | x | x | 2 | delete_mc_IP_address | double_long_unsigned |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
|  | x | x | 3 | get_nbof_mc_IP_addresses | unsigned |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
|  | x | x
|  | x | x |  | IPv6 setup |  | 48 | 0 | 0-0:25.7.0.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000190700FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | DL_reference | octet_string[6] |  |  | 0-0:25.3.0.255 | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 3 | address_config_mode | enum |  |  | 0 | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 4 | unicast_IPv6_addresses | array[0..*](IPv6_address) |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 5 | multicast_IPv6_addresses | array[0..*](IPv6_address) |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 6 | gateway_IPv6_address | array[0..*](IPv6_address) |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 7 | primary_DNS_address | IPv6_address |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 8 | secondary_DNS_address | IPv6_address |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 9 | traffic_class | unsigned |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 10 | neighbor_discovery_setup | array[0..*](neighbour_discovery_setup_element) |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 1 | add_IPv6_address | IPv6_address_entry |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
|  | x | x | 2 | remove_IPv6_address | IPv6_address_entry |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
|  | x | x
|  | x | x |  | PPP setup |  | 44 | 0 | 0-0:25.3.0.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000190300FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | PHY_refernce | octet_string[6] |  |  | 0-0:25.4.0.255 | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 3 | LCP_options | array[1..8](LCP_options_element) |  |  | { {3, 4, 0xC023},... } | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | { LCP-option-type := Auth-Prot, LCP-Option-Length := 2, LCP-option-data := PAP}
|  | x | x | 4 | IPCP_options | array[1..5](IPCP_options_element) |  |  | { {2, 4, 0x0000},... } | -- | -- | Get | Get | -- | -- | -- | Get | { IPCP-option-type := IP-comp-prot, IPCP-option-Length := 2, IPCP-option-data := No-IP-Compresion-is-used}
|  | x | x | 5 | PPP_authentication | PPP_authentication_type |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | { choice( NULL, { user-name, PAP-password} ) }
|  | x | x
x | x | x | x |  | Abstract objects - Push setup
x | x |  |  |  | Push setup - Interval_1 |  | 40 | 0 | 0-1:25.9.0.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "0001190900FF" | -- | -- | Get | Get | -- | -- | -- | Get
x | x |  |  | 2 | push_object_list | array[0..20…*](capture_object_definition) |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set
x | x |  |  | 3 | send_destination_and_method | send_destination_and_method_type |  |  | {1,[x:x:x:x:x:x:x:x]:y,0} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Contains the destination address where the data specified by the push_object_list has to be sent, as well as the sending method. Autorised values: - TCP, IPv4, A-XDR => {0, x.x.x.x:y, 0} - TCP, IPv6, A-XDR => {0, [x:x:x:x:x:x:x:x]:y, 0} - UDP, IPv6, A-XDR => {1,[x:x:x:x:x:x:x:x]:y,0} Default value: {1,[x:x:x:x:x:x:x:x]:y,0}
x | x |  |  | 4 | communication_window | array[0..1](window_element) |  |  |  | -- | -- | -- | Get, Set | -- | -- | -- | Get, Set | up to one window can be supported default: empty
x | x |  |  | 5 | randomisation_start_interval | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
x | x |  |  | 6 | number_of_retries | unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
x | x |  |  | 7 | repetition_delay | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Delay in seconds between repetitions
x | x |  |  | 1 | push | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x
|  | x | x |  | Push setup - Interval_1 |  | 40 | 0 | 0-1:25.9.0.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0001190900FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | push_object_list | array[0..20…*](capture_object_definition) |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set
|  | x | x | 3 | send_destination_and_method | send_destination_and_method_type |  |  | {0, x.x.x.x:y, 0} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Contains the destination address where the data specified by the push_object_list has to be sent, as well as the sending method. Autorised values: - TCP, IPv4, A-XDR => {0, x.x.x.x:y, 0} - TCP, IPv6, A-XDR => {0, [x:x:x:x:x:x:x:x]:y, 0} - UDP, IPv6, A-XDR => {1,[x:x:x:x:x:x:x:x]:y,0} Default value: {0, x.x.x.x:y, 0}
|  | x | x | 4 | communication_window | array[0..1](window_element) |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | up to one window can be supported default: empty
|  | x | x | 5 | randomisation_start_interval | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
|  | x | x | 6 | number_of_retries | unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
|  | x | x | 7 | repetition_delay | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Delay in seconds between repetitions
|  | x | x | 1 | push | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
|  | x | x
x | x |  |  |  | Push setup - Interval_2 |  | 40 | 0 | 0-2:25.9.0.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "0002190900FF" | -- | -- | Get | Get | -- | -- | -- | Get
x | x |  |  | 2 | push_object_list | array[0..20..*](capture_object_definition) |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set
x | x |  |  | 3 | send_destination_and_method | send_destination_and_method_type |  |  | {1,[x:x:x:x:x:x:x:x]:y,0} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Contains the destination address where the data specified by the push_object_list has to be sent, as well as the sending method. Autorised values: - TCP, IPv4, A-XDR => {0, x.x.x.x:y, 0} - TCP, IPv6, A-XDR => {0, [x:x:x:x:x:x:x:x]:y, 0} - UDP, IPv6, A-XDR => {1,[x:x:x:x:x:x:x:x]:y,0} Default value: {1,[x:x:x:x:x:x:x:x]:y,0}
x | x |  |  | 4 | communication_window | array[0..1](window_element) |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | up to one window can be supported default: empty
x | x |  |  | 5 | randomisation_start_interval | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
x | x |  |  | 6 | number_of_retries | unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
x | x |  |  | 7 | repetition_delay | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Delay in seconds between repetitions
x | x |  |  | 1 | push | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x
|  | x | x |  | Push setup - Interval_2 |  | 40 | 0 | 0-2:25.9.0.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0002190900FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | push_object_list | array[0..20..*](capture_object_definition) |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set
|  | x | x | 3 | send_destination_and_method | send_destination_and_method_type |  |  | {0, x.x.x.x:y, 0} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Contains the destination address where the data specified by the push_object_list has to be sent, as well as the sending method. Autorised values: - TCP, IPv4, A-XDR => {0, x.x.x.x:y, 0} - TCP, IPv6, A-XDR => {0, [x:x:x:x:x:x:x:x]:y, 0} - UDP, IPv6, A-XDR => {1,[x:x:x:x:x:x:x:x]:y,0} Default value: {0, x.x.x.x:y, 0}
|  | x | x | 4 | communication_window | array[0..1](window_element) |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | up to one window can be supported default: empty
|  | x | x | 5 | randomisation_start_interval | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
|  | x | x | 6 | number_of_retries | unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
|  | x | x | 7 | repetition_delay | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Delay in seconds between repetitions
|  | x | x | 1 | push | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
|  | x | x
x | x |  |  |  | Push setup - Interval_3 |  | 40 | 0 | 0-3:25.9.0.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "0003190900FF" | -- | -- | Get | Get | -- | -- | -- | Get
x | x |  |  | 2 | push_object_list | array[0..20..*](capture_object_definition) |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set
x | x |  |  | 3 | send_destination_and_method | send_destination_and_method_type |  |  | {1,[x:x:x:x:x:x:x:x]:y,0} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Contains the destination address where the data specified by the push_object_list has to be sent, as well as the sending method. Autorised values: - TCP, IPv4, A-XDR => {0, x.x.x.x:y, 0} - TCP, IPv6, A-XDR => {0, [x:x:x:x:x:x:x:x]:y, 0} - UDP, IPv6, A-XDR => {1,[x:x:x:x:x:x:x:x]:y,0} Default value: {1,[x:x:x:x:x:x:x:x]:y,0}
x | x |  |  | 4 | communication_window | array[0..1](window_element) |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | up to one window can be supported default: empty
x | x |  |  | 5 | randomisation_start_interval | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
x | x |  |  | 6 | number_of_retries | unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
x | x |  |  | 7 | repetition_delay | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Delay in seconds between repetitions
x | x |  |  | 1 | push | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x
|  | x | x |  | Push setup - Interval_3 |  | 40 | 0 | 0-3:25.9.0.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0003190900FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | push_object_list | array[0..20..*](capture_object_definition) |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set
|  | x | x | 3 | send_destination_and_method | send_destination_and_method_type |  |  | {0, x.x.x.x:y, 0} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Contains the destination address where the data specified by the push_object_list has to be sent, as well as the sending method. Autorised values: - TCP, IPv4, A-XDR => {0, x.x.x.x:y, 0} - TCP, IPv6, A-XDR => {0, [x:x:x:x:x:x:x:x]:y, 0} - UDP, IPv6, A-XDR => {1,[x:x:x:x:x:x:x:x]:y,0} Default value: {0, x.x.x.x:y, 0}
|  | x | x | 4 | communication_window | array[0..1](window_element) |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | up to one window can be supported default: empty
|  | x | x | 5 | randomisation_start_interval | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
|  | x | x | 6 | number_of_retries | unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
|  | x | x | 7 | repetition_delay | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Delay in seconds between repetitions
|  | x | x | 1 | push | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
|  | x | x
x | x |  |  |  | Push setup - On Alarm |  | 40 | 0 | 0-4:25.9.0.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "0004190900FF" | -- | -- | Get | Get | -- | -- | -- | Get
x | x |  |  | 2 | push_object_list | array[0..20..*](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:97.98.20.255,2,0}, {1,0-0:97.98.21.255,2,0}, {1,0-0:97.98.22.255,2,0}} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set
x | x |  |  | 3 | send_destination_and_method | send_destination_and_method_type |  |  | {1,[x:x:x:x:x:x:x:x]:y,0} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Contains the destination address where the data specified by the push_object_list has to be sent, as well as the sending method. Autorised values: - TCP, IPv4, A-XDR => {0, x.x.x.x:y, 0} - TCP, IPv6, A-XDR => {0, [x:x:x:x:x:x:x:x]:y, 0} - UDP, IPv6, A-XDR => {1,[x:x:x:x:x:x:x:x]:y,0} Default value: {1,[x:x:x:x:x:x:x:x]:y,0}
x | x |  |  | 4 | communication_window | array[0..1](window_element) |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | up to one window can be supported default: empty
x | x |  |  | 5 | randomisation_start_interval | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
x | x |  |  | 6 | number_of_retries | unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
x | x |  |  | 7 | repetition_delay | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Delay in seconds between repetitions
x | x |  |  | 1 | push | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x
|  | x | x |  | Push setup - On Alarm |  | 40 | 0 | 0-4:25.9.0.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0004190900FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | push_object_list | array[0..20..*](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:97.98.20.255,2,0}, {1,0-0:97.98.21.255,2,0}, {1,0-0:97.98.22.255,2,0}} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set
|  | x | x | 3 | send_destination_and_method | send_destination_and_method_type |  |  | {0, x.x.x.x:y, 0} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Contains the destination address where the data specified by the push_object_list has to be sent, as well as the sending method. Autorised values: - TCP, IPv4, A-XDR => {0, x.x.x.x:y, 0} - TCP, IPv6, A-XDR => {0, [x:x:x:x:x:x:x:x]:y, 0} - UDP, IPv6, A-XDR => {1,[x:x:x:x:x:x:x:x]:y,0} Default value: {0, x.x.x.x:y, 0}
|  | x | x | 4 | communication_window | array[0..1](window_element) |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | up to one window can be supported default: empty
|  | x | x | 5 | randomisation_start_interval | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
|  | x | x | 6 | number_of_retries | unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
|  | x | x | 7 | repetition_delay | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Delay in seconds between repetitions
|  | x | x | 1 | push | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
|  | x | x
x | x |  |  |  | Push setup - On Connectivity |  | 40 | 0 | 0-0:25.9.0.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "0000190900FF" | -- | -- | Get | Get | -- | -- | -- | Get
x | x |  |  | 2 | push_object_list | array[0..20..*](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.1.0.255,2,0}, {48,0-0:25.7.0.255,4,2}} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | default capture objects for PLC meters - clock - device ID 1 - IPv6 address (index 2 for the ULA address)
x | x |  |  | 3 | send_destination_and_method | send_destination_and_method_type |  |  | {1,[x:x:x:x:x:x:x:x]:y,0} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Contains the destination address where the data specified by the push_object_list has to be sent, as well as the sending method. Autorised values: - TCP, IPv4, A-XDR => {0, x.x.x.x:y, 0} - TCP, IPv6, A-XDR => {0, [x:x:x:x:x:x:x:x]:y, 0} - UDP, IPv6, A-XDR => {1,[x:x:x:x:x:x:x:x]:y,0} Default value: {1,[x:x:x:x:x:x:x:x]:y,0}
x | x |  |  | 4 | communication_window | array[0..1](window_element) |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | up to one window can be supported default: empty
x | x |  |  | 5 | randomisation_start_interval | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
x | x |  |  | 6 | number_of_retries | unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
x | x |  |  | 7 | repetition_delay | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Delay in seconds between repetitions
x | x |  |  | 1 | push | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x
|  | x | x |  | Push setup - On Connectivity |  | 40 | 0 | 0-0:25.9.0.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000190900FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | push_object_list | array[0..20..*](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.1.0.255,2,0}, {48,0-0:25.7.0.255,4,0}, {42,0-0:25.1.0.255,3,0}} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | default capture objects for PLC meters - clock - device ID 1 - IPv6 address - IPv4 address
|  | x | x | 3 | send_destination_and_method | send_destination_and_method_type |  |  | {0, x.x.x.x:y, 0} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Contains the destination address where the data specified by the push_object_list has to be sent, as well as the sending method. Autorised values: - TCP, IPv4, A-XDR => {0, x.x.x.x:y, 0} - TCP, IPv6, A-XDR => {0, [x:x:x:x:x:x:x:x]:y, 0} - UDP, IPv6, A-XDR => {1,[x:x:x:x:x:x:x:x]:y,0} Default value: {1,[x:x:x:x:x:x:x:x]:y,0}
|  | x | x | 4 | communication_window | array[0..1](window_element) |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | up to one window can be supported default: empty
|  | x | x | 5 | randomisation_start_interval | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
|  | x | x | 6 | number_of_retries | unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
|  | x | x | 7 | repetition_delay | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Delay in seconds between repetitions
|  | x | x | 1 | push | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
|  | x | x
x | x |  |  |  | Push setup - On Installation |  | 40 | 0 | 0-7:25.9.0.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "0007190900FF" | -- | -- | Get | Get | -- | -- | -- | Get
x | x |  |  | 2 | push_object_list | array[0..20..*](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.1.0.255,2,0}, {48,0-0:25.7.0.255,4,2}} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | default capture objects for PLC meters - clock - device ID 1 - IPv6 address (index 2 for the ULA address)
x | x |  |  | 3 | send_destination_and_method | send_destination_and_method_type |  |  | {1,[x:x:x:x:x:x:x:x]:y,0} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Contains the destination address where the data specified by the push_object_list has to be sent, as well as the sending method. Autorised values: - TCP, IPv4, A-XDR => {0, x.x.x.x:y, 0} - TCP, IPv6, A-XDR => {0, [x:x:x:x:x:x:x:x]:y, 0} - UDP, IPv6, A-XDR => {1,[x:x:x:x:x:x:x:x]:y,0} Default value: {1,[x:x:x:x:x:x:x:x]:y,0}
x | x |  |  | 4 | communication_window | array[0..1](window_element) |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | up to one window can be supported default: empty
x | x |  |  | 5 | randomisation_start_interval | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
x | x |  |  | 6 | number_of_retries | unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
x | x |  |  | 7 | repetition_delay | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Delay in seconds between repetitions
x | x |  |  | 1 | push | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
x | x
|  | x | x |  | Push setup - On Installation |  | 40 | 0 | 0-7:25.9.0.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0007190900FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | push_object_list | array[0..20..*](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.1.0.255,2,0}, {48,0-0:25.7.0.255,4,0}, {42,0-0:25.1.0.255,3,0}} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | default capture objects for PLC meters - clock - device ID 1 - IPv6 address - IPv4 address
|  | x | x | 3 | send_destination_and_method | send_destination_and_method_type |  |  | {0, x.x.x.x:y, 0} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Contains the destination address where the data specified by the push_object_list has to be sent, as well as the sending method. Autorised values: - TCP, IPv4, A-XDR => {0, x.x.x.x:y, 0} - TCP, IPv6, A-XDR => {0, [x:x:x:x:x:x:x:x]:y, 0} - UDP, IPv6, A-XDR => {1,[x:x:x:x:x:x:x:x]:y,0} Default value: {0, x.x.x.x:y, 0}
|  | x | x | 4 | communication_window | array[0..1](window_element) |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | up to one window can be supported default: empty
|  | x | x | 5 | randomisation_start_interval | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Randomiztion time in seconds, 0 = no randomization at start of the first window defined in calling_window
|  | x | x | 6 | number_of_retries | unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Max number of repetitions of unsuccessful push
|  | x | x | 7 | repetition_delay | long_unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Delay in seconds between repetitions
|  | x | x | 1 | push | integer |  |  |  | -- | -- | Action | Action | -- | -- | -- | Action
|  | x | x
x | x | x | x |  | Push script table |  | 9 | 0 | 0-0:10.0.108.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00000A006CFF" | -- | -- | -- | Get | -- | -- | -- | Get
x | x | x | x | 2 | scripts | scripts |  |  | { {1,{{2,40,0-1:25.9.0.255,1,0}}}, //Push - Interval_1 {2,{{2,40,0-2:25.9.0.255,1,0}}}, //Push - Interval_2 {3,{{2,40,0-3:25.9.0.255,1,0}}}, //Push - Interval_3 {4,{{2,40,0-4:25.9.0.255,1,0}}}, //Push - On Alarm {5,{{2,40,0-0:25.9.0.255,1,0}}}, //Push - On Connectivity {6,{{2,40,0-7:25.9.0.255,1,0}}}, //Push - On Installation {7,{{2,40,0-5:25.9.0.255,1,0}}}, //Push - On Power Down {8,{{2,40,0-6:25.9.0.255,1,0}}}, //Push - Consumer Information } | -- | -- | -- | Get | -- | -- | -- | Get | The first 6 scripts are mandatory, script 7 and 8 only need to be present if the optional elements (push setup on power down and CIP) are present as well. Please note that the assignment of the script_identifier is fixed.
x | x | x | x | 1 | execute | long_unsigned |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action
x | x | x | x
x | x | x | x |  | Push action scheduler - Interval_1 |  | 22 | 0 | 0-1:15.0.4.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00010F0004FF" | -- | -- | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | executed_script | script22 |  |  | {0-0:10.0.108.255,1} | -- | -- | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | type | enum |  |  | 5 | -- | -- | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | execution_time | array[0..4](execution_time_date) |  |  | {} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set
x | x | x | x
x | x | x | x |  | Push action scheduler - Interval_2 |  | 22 | 0 | 0-2:15.0.4.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00020F0004FF" | -- | -- | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | executed_script | script22 |  |  | {0-0:10.0.108.255,2} | -- | -- | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | type | enum |  |  | 5 | -- | -- | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | execution_time | array[0..4](execution_time_date) |  |  | {} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set
x | x | x | x
x | x | x | x |  | Push action scheduler - Interval_3 |  | 22 | 0 | 0-3:15.0.4.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "00030F0004FF" | -- | -- | Get | Get | -- | -- | -- | Get
x | x | x | x | 2 | executed_script | script22 |  |  | {0-0:10.0.108.255,3} | -- | -- | Get | Get | -- | -- | -- | Get
x | x | x | x | 3 | type | enum |  |  | 5 | -- | -- | Get | Get | -- | -- | -- | Get
x | x | x | x | 4 | execution_time | array[0..4](execution_time_date) |  |  | {} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set
x | x | x | x
x | x | x | x |  | Remote communication - Abstract Objects for Network Mgmt
x | x | x | x |  | Auto connect |  | 29 | 2 | 0-0:2.1.0.255
x | x | x | x | 1 | logical_name | octet_string[6] |  |  | "0000020100FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x | x | x | 2 | mode | enum |  |  | 101 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | (101) The meter is permanently connected to the IP network and can be reached by the client via its known IP address. (104) The meter is usually disconnected. It connects to the IP network when the connect method is invoked. If the HES needs to communicate to the meter the HES shall wake-up the meter via SMS.
x | x | x | x | 3 | repetitions | unsigned |  |  | 0 | -- | -- | Get | Get | -- | -- | Get | Get
x | x | x | x | 4 | repetition_delay | long_unsigned |  |  | 0 | -- | -- | Get | Get | -- | -- | Get | Get
x | x | x | x | 5 | calling_window | array[0..*](window_element) |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get
x | x | x | x | 6 | destination_list | array[0..*] |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get
x | x | x | x | 1 | connect | integer |  |  |  | -- | -- | Action | Action | -- | -- | Action | Action
x | x | x | x
x | x |  |  |  | MAC address setup |  | 43 | 0 | 0-0:25.2.0.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "0000190200FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | MAC_address | octet_string |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | The MAC address setup holds the EUI-48 address of the PLC G3 Modem.
x | x
|  | x | x |  | Remote communication - GSM/GPRS Setup Objects
|  | x | x |  | Modem Hardware version |  | 1 | 0 | 0-5:96.1.0.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0005600100FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | octet_string[0..48] |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x
|  | x | x |  | Modem Manufacturer |  | 1 | 0 | 0-5:96.1.2.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0005600102FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | octet_string[0..48] |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x
|  | x | x |  | Modem setup |  | 45 | 0 | 0-0:25.4.0.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000190400FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | APN | octet_string[0..64] |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | An APN with a size of 64 bytes at least is supported, i.e. [0.64] is mandatoty but can be longer
|  | x | x | 3 | PIN_code | long_unsigned |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
|  | x | x | 4 | quality_of_service | quality_of_service_type |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x
|  | x | x |  | Message Handler |  | 8192 | 0 | 0-0:2.130.0.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000028200FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | Listening_window | structure |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | In case SMS wakeup is used: Listening_window is always active. In case SMS wakeup is not used: Listening window is never active. Value Listening_window ::= structure { start_time: octet string end_time: octet string }
|  | x | x | 3 | Message_content | octet string |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set
|  | x | x | 4 | list_of_senders_and_actions | array |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Array of senders with associated scripts. The script contains the push method invocation of the Push Setup on connectivity
|  | x | x
|  | x | x |  | PHY Randomization Object |  | 1 | 0 | 0-1:94.31.12.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "00015E1F0CFF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | structure |  |  | {240; 2; 6; 1} | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | The waiting time procedure for re-registration of the modem to the network is configured and managed. Value ::= structure { randomisation_start_window double-long-unsigned, multiplication_factor long-unsigned, number_of_retries long-unsigned, direct_attach_at_power_on_flag boolean, }
|  | x | x
|  | x | x |  | Modem Reset Timer |  | 1 | 0 | 0-1:94.31.2.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "00015E1F02FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | long_unsigned |  |  | 24 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | The power-off-on reset cycle of the modem when the timer expires is configured and managed.
|  | x | x
|  | x | x |  | Network Status Check Timer |  | 1 | 0 | 0-1:94.31.3.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "00015E1F03FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | long_unsigned |  |  | 1 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | The time interval for checking the network status of the modem is configured and managed.
|  | x | x
|  | x | x |  | Periodic Ping Configuration |  | 1 | 0 | 0-1:94.31.5.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "00015E1F05FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | structure |  |  | { ""; 30; 3; 3; 3 } | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | The time interval for sending between modem and central system can be configured and managed Value ::= structure { Ping Destination Octet string, Ping Timer long-unsigned, Num-pings long-unsigned, (range 1-100) Multiplication_factor long-unsigned, (range 1-100) Number_of_retries long-unsigned, (range 1-100) } The Ping Timer unit is minutes.
|  | x | x
|  | x | x |  | Connection Watchdog Timer |  | 1 | 0 | 0-1:94.31.7.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "00015E1F07FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | long_unsigned |  |  | 6 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | A watchdog timer makes sure that the modem is reset after a defined period of no contact with the CS.
|  | x | x
|  | x | x |  | Periodical Self-Check Timer |  | 1 | 0 | 0-1:94.31.10.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "00015E1F0AFF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | long_unsigned |  |  | 1440 | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | The time interval for initiating a self-check of the modem can be configured and managed
|  | x | x
|  | x | x |  | GSM diagnostic |  | 47 | 1 | 0-0:25.6.0.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000190600FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | operator | octet_string[0..64] |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 3 | status | enum |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get | Indicates the registration status of the modem. enum: (0) not registered, (1) registered, home network, (2) not registered, but MT is currently searching a new operator to register to, (3) registration denied, (4) unknown, (5) registered, roaming (6) ... (255) reserved
|  | x | x | 4 | cs_attachment | enum |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get | Indicates the current circuit switched status. enum: (0) inactive, (1) incoming call, (2) active, (3) ... (255) reserved
|  | x | x | 5 | ps_status | enum |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get | The ps_status value field indicates the packet switched status of the modem. enum: (0) inactive, (1) GPRS, (2) EDGE, (3) UMTS, (4) HSDPA, (5) LTE, (6) CDMA, (7) ... (255) reserved
|  | x | x | 6 | cell_info | cell_info_type |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get | Represents the cell information: - cell_ID: Four-byte cell ID in hexadecimal format; - location_ID: Two-byte location area code (LAC) in the case of GSM networks or Tracking Area Code (TAC) in the case of UMTS, CDMA or LTE networks in hexadecimal format (e.g. "00C3" equals 195 in decimal); - signal_quality: Represents the signal quality: (0) –113 dBm or less, (1) –111 dBm, (2...30) –109…-53 dBm, (31) –51 or greater, (99) not known or not detectable; - ber: Bit error rate (BER) measurement in percent: (0…7) as RXQUAL_n values specified in ETSI GSM 05.08 8.2.4. (99) not known or not detectable. - mcc: Mobile Country Code of the serving network, as defined in ITU-T E.212 (05.2008); - mnc: Mobile Network Code of the serving network, as defined in ITU-T E.212 (05.2008); - channel_number: Represents the absolute radio-frequency channel number (ARFCN or eaRFCN for LTE network).
|  | x | x | 7 | adjacent_cells | structure { cell_ID: double_long_unsigned; signal_quality: unsigned } |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get | - cell_ID: Four-byte cell ID in hexadecimal format; - signal_quality: Represents the signal quality: (0) –113 dBm or less, (1) –111 dBm, (2...30) –109…-53 dBm, (31) –51 or greater, (99) not known or not detectable.
|  | x | x | 8 | capture_time | array[0..*](list_of_allowed_callers_element) |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get | phone number is an ASCII coded octet-string of phone number length
|  | x | x
|  | x | x |  | P2P Communication Error Code |  | 1 | 0 | 0-0:97.98.3.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000616203FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x
|  | x | x |  | Bytes Sent In A Configurable Interval |  | 1 | 0 | 0-0:96.12.132.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600C84FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x
|  | x | x |  | Bytes Received In A Configurable Interval |  | 1 | 0 | 0-0:96.12.133.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600C85FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x
|  | x | x |  | Bytes Sent total |  | 1 | 0 | 0-0:96.12.134.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600C84FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | long64_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x
|  | x | x |  | Bytes Received total |  | 1 | 0 | 0-0:96.12.135.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000600C85FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | long64_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x
|  | x | x |  | Communication Throughput Profile |  | 7 | 1 | 0-0:99.98.12.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "000063620CFF" | -- | Get | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
|  | x | x | 3 | capture_objects | array |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:96.12.132.255,2,0}, {1,0-0:96.12.133.255,2,0}} | -- | Get | Get | Get | -- | -- | -- | Get | clock; bytes sent in a configurable interval; bytes received in a configurable interval
|  | x | x | 4 | capture_period | double_long_unsigned |  |  | 3600 | -- | Get | Get | Get | -- | -- | -- | Get
|  | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
|  | x | x | 6 | sort_object | capture_object_definition |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
|  | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
|  | x | x | 8 | profile_entries | double_long_unsigned |  |  | 60 | -- | Get | Get | Get | -- | -- | -- | Get
|  | x | x | 1 | reset |  |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res -
|  | x | x | 2 | capture |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
|  | x | x
|  | x | x |  | Average RTT |  | 1 | 0 | 0-1:94.31.13.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000601F0DFF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | long-unsigned |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get | Indicates the round-trip time interval Unit=millisecond
|  | x | x
|  | x | x |  | Number of ping responses that were received |  | 1 | 0 | 0-1:94.31.14.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000601F0EFF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | long-unsigned |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get | Indicate the number of reply frames received
|  | x | x
|  | x | x |  | RTT Sessions Event Log |  | 7 | 1 | 0-0:99.98.14.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "000063620EFF" | -- | Get | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
|  | x | x | 3 | capture_objects | array |  |  | {{8,0-0:1.0.0.255,2,0}, {1, 0-1:94.31.13,255,2,0}, {1, 0-1:94.31.14,255,2,0}}; | -- | Get | Get | Get | -- | -- | -- | Get | clock; Average RTT; Number of ping responses that were received
|  | x | x | 4 | capture_period | double_long_unsigned |  |  | 0, asynchronously | -- | Get | Get | Get | -- | -- | -- | Get
|  | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
|  | x | x | 6 | sort_object | capture_object_definition |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
|  | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
|  | x | x | 8 | profile_entries | double_long_unsigned |  |  | 60 | -- | Get | Get | Get | -- | -- | -- | Get
|  | x | x | 1 | reset | integer |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res -
|  | x | x | 2 | capture |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
|  | x | x
|  | x | x |  | Reference Signal Receiving Power |  | 1 | 0 | 0-1:94.31.18.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000601F12FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | long |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get | Indicates the signal strength of the LTE network
|  | x | x
|  | x | x |  | Reference Signal Receiving Quality |  | 1 | 0 | 0-1:94.31.19.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000601F13FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | long |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get | Indicates the quality of LTE reference signal reception, and mainly used for cell reselection and sorting in LTE networks
|  | x | x
|  | x | x |  | Network Information |  | 1 | 0 | 0-1:94.31.4.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "00015E1F04FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | structure |  |  |  | -- | -- | Get | Get | -- | -- | -- | Get | The moderm information description of present moderm status. Value ::= structure { signal_strength integer, bit_error_rate integer, number_of_base_stations integer, IMSI octet string, IMEI octet string, MSISDN octet string, ICCID octet string, Main_Cell_ID double-long-unsigned, }
|  | x | x
|  | x | x |  | Network Condition Profile |  | 7 | 1 | 0-0:99.12.0.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "0000630C00FF" | -- | Get | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | buffer | array |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
|  | x | x | 3 | capture_objects | array |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-1:94.31.4.255,2,1}, {1,0-1:94.31.4.255,2,2}, {1, 0-1:94.31.18.255,2,0}, {1, 0-1:94.31.19.255,2,0}} | -- | Get | Get | Get | -- | -- | -- | Get | clock;signal_strength; bit_error_rate
|  | x | x | 4 | capture_period | double_long_unsigned |  |  | 600 | -- | Get | Get, Set | Get, Set | -- | -- | -- | Get, Set
|  | x | x | 5 | sort_method | enum |  |  | 1 | -- | Get | Get | Get | -- | -- | -- | Get | unsorted (FIFO)
|  | x | x | 6 | sort_object | capture_object_definition |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
|  | x | x | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | Get | Get | Get | -- | -- | -- | Get
|  | x | x | 8 | profile_entries | double_long_unsigned |  |  | 60 | -- | Get | Get | Get | -- | -- | -- | Get
|  | x | x | 1 | reset |  |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action Req S, Res -
|  | x | x | 2 | capture |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
|  | x | x
|  | x | x |  | FOTA image FTPS Server Address |  | 1 | 0 | 0-1:94.31.15.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "00015E1F0FFF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | structure |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Value ::= structure { FSTP Server IP Address octet-string, FSTP Server TCP Port long-unsigned, }
|  | x | x
|  | x | x |  | FOTA Image FTPS Server Access Credential |  | 1 | 0 | 0-1:94.31.16.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "00015E1F10FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | structure |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Value ::= structure { User name Octet string, Password Octet string, }
|  | x | x
|  | x | x |  | FOTA Firmware Upgrade Image File Name |  | 1 | 0 | 0-1:94.31.17.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "00015E1F11FF" | -- | -- | Get | Get | -- | -- | -- | Get
|  | x | x | 2 | value | structure |  |  |  | -- | -- | Get, Set | Get, Set | -- | -- | -- | Get, Set | Value ::= structure { New Image File Name Octet string, Fallback Image File Name Octet string, }
|  | x | x
|  | x | x |  | FOTA Firmware Upgrade Script Table |  | 9 | 0 | 0-0:10.1.107.255
|  | x | x | 1 | logical_name | octet_string[6] |  |  | "00000A016BFF" | -- | -- | -- | Get | -- | -- | -- | Get
|  | x | x | 2 | scripts | scripts |  |  |  | -- | -- | -- | Get | -- | -- | -- | Get | Script 1 initiates the firmware upgrade process Script 2 initiates the firmware fallback process
|  | x | x | 1 | execute | long_unsigned |  |  |  | -- | -- | -- | Action | -- | -- | -- | Action | Data contains the entry in the script table (1 or 2)
|  | x | x
x | x |  |  |  | Remote communication - G3-PLC Setup Objects
x | x |  |  |  | PLCG3_Bandplan |  | 1 | 0 | 0-0:94.43.128.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E2B80FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | enum |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | This object allows the identification of the current bandplan in use. Switching between Cenelec A and FCC band must be possible by either FW upgrade or configuration change: - In case of using a FW upgrade, this object shall be declared as readable only and displays the currently bandplan in use. - In case of using a configuration change, this object shall be declared as readable and writable and allows changing the current bandplan in use. Data type: ENUMERATED Authorized values: 0 = CENELEC-A band 3 = FCC band Default value: 0
x | x
x | x |  |  |  | PLCG3_Bandplan scheduler |  | 22 | 0 | 0-0:94.43.129.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E2B81FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | executed_script | script22 |  |  | {0-0:94.43.130.255, 1} | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | Bandplan activation script of PLCG3_Bandplan script table (0-0:94.43.130.255) Authorized value: 1 to 2 (CENELC-A or FCC)
x | x |  |  | 3 | type | enum |  |  | 1 | -- | -- | Get | Get | -- | -- | Get | Get | only type 1 is supported
x | x |  |  | 4 | execution_time | array[0..1](execution_time_date) |  |  | {} | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | dedicated timepoint for connection or disconnection; the execution can be disabled with writing empty array or {{"FFFFFFFF", "FFFFFFFFFF"}}
x | x
x | x |  |  |  | PLCG3_Bandplan script table |  | 9 | 0 | 0-0:94.43.130.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E2B82FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | scripts | array[2](script9) |  |  | { {1,{1,1,0-0:94.43.128.255,2,0}}, //set Bandplan to CENELEC-A {2,{1,1,0-0:94.43.128.255,2,3}}, //set Bandplan to FCC } | -- | -- | Get | Get | -- | -- | Get | Get | Bandplan activation scripts, 1 sets Bandplan to CENELEC-A 2 sets Bandplan to FCC
x | x |  |  | 1 | execute | long_unsigned |  |  |  | -- | -- | Action | Action | -- | -- | Action | Action | Executes the script specified in parameter data. If data matches one of the script_identifiers in the script table, then the corresponding action_specification is executed.
x | x
x | x |  |  |  | PLCG3_PSK_KEK |  | 1 | 0 | 0-0:94.43.133.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E2B85FF" | -- | -- | -- | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | octet_string |  |  |  | -- | -- | -- | Set | -- | -- | Set Req S, Res - | Set Req S, Res - | This object allows changing the PSK Key Encryption Key of the meter. The new PSK_KEK must use the AES-128 key wrap algorithm using the current PSK_KEK as the wrapping key.
x | x
x | x |  |  |  | PLCG3_PSK |  | 1 | 0 | 0-0:94.33.128.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E2180FF" | -- | -- | -- | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | octet_string |  |  |  | -- | -- | -- | Set | -- | -- | Set Req S, Res - | Set Req S, Res - | This object allows changing the PSK of the meter. The new PSK is wrapped by the AES-128 key wrap algorithm, using the PLCG3_PSK_KEK as the wrapping key. After the successful change of the PSK (confirmation to the DLMS client), the meter returns to the non associated state and re-starts it’s joining process for the reconnection to the PAN coordinator
x | x
x | x |  |  |  | PLCG3TimeOut |  | 1 | 0 | 0-0:94.33.10.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E210AFF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | long_unsigned |  |  | 360 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | This data defines the time, in minutes, after which a meter that has not been individually addressed (meaning the meter has not received any Path Discovery message, ICMP ping, nor unicast DLMS APDU) returns to the non associated state and loses its PAN coordinator. A value equal to 0 is equivalent to cancel the use of the related time-out-not-addressed counter. value Authorized value: 0 to 65535
x | x
x | x |  |  |  | PLCG3KeepAlive |  | 1 | 0 | 0-0:94.33.11.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E210BFF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | structure { keep_alive_enable keep_alive_start_time keep_alive_send_period } |  |  | { 0;300;10} | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | keep_alive_enable This parameter indicates whether the keep alive mechanism is enabled or not. Data type: BOOLEAN Authorized value: 0: FALSE The keep alive mechanism is disabled 1: TRUE The keep alive mechanism is enabled Default value: 0 keep_alive_start_time This parameter indicates the time in minutes to wait before starting the periodic emission of ICMP Echo requests. Data type: UNSIGNED16 Authorized value: 0 to 65535 Default value: 300 keep_alive_send_period This parameter indicates the time in minutes between two successive keep alive ICMP Echo requests. Data type: UNSIGNED8 Authorized value: 1 to 255 Default value: 10
x | x
x | x |  |  |  | G3-PLC MAC 6LoWPAN adaptation layer setup |  | 92 | 1 | 0-0:29.2.0.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00001D0200FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | adp_max_hops | unsigned |  |  | 14 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | These attribute defines the maximum number of hops to be used by the routing algorithm. Data type: UNSIGNED8 Authorized value: 1 to 14 Default value: 14
x | x |  |  | 3 | adp_weak_LQI_value | unsigned |  |  | 52 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | The weak link value defines the LQI value below which a link to a neighbour is considered as a weak link Data type: UNSIGNED8 Authorized value: 0 to 255 Default value: 52
x | x |  |  | 4 | adp_security_level | unsigned |  |  | 5 | -- | -- | Get | Get | -- | -- | Get | Get | The minimum security level to be used for incoming and outgoing adaptation frames. Data type: UNSIGNED8 Authorized value: 0: no ciphering 5: ciphering with 32 bits integrity code
x | x |  |  | 5 | adp_prefix_table | array[0..4] (prefix_entry) prefix_entry: struct { prefix_length: unsigned L: unsigned A: unsigned valid_lifetime: double_long_unsigned preferred_lifetime: double_long_unsigned prefix: octet_string[16] } } |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | prefix_length Number of leading bits in the Prefix that are valid. Data type: UNSIGNED8 Authorized value: 0 to 128 L 1-bit on-link flag. Data type: UNSIGNED8 Authorized value: 0 to 1 A 1-bit autonomous address-configuration flag. Data type: UNSIGNED8 Authorized value: 0 to 1 valid_lifetime time in seconds during which the prefix is valid for the purpose of on-link determination. Data type: UNSIGNED32 Authorized value: 0 to 4294967295 preferred_lifetime time in seconds during which addresses generated from the prefix remain preferred. Data type: UNSIGNED32 Authorized value: 0 to 4294967295 prefix IPv6 address or a prefix of an IPv6 address Data type: Data type: OCTETSTRING
x | x |  |  | 6 | adp_routing_configuration | array[1] (routing_configuration) routing_configuration::= structure { adp_net_traversal_time: unsigned, adp_routing_table_entry_TTL: long-unsigned, adp_Kr: unsigned, adp_Km: unsigned, adp_Kc: unsigned, adp_Kq: unsigned, adp_Kh: unsigned, adp_Krt: unsigned, adp_RREQ_retries: unsigned, adp_RREQ_wait: unsigned, adp_blacklist_table_entry_TTL: long-unsigned, adp_unicast_RREQ_gen_enable: boolean, adp_RLC_Enabled: boolean, adp_add_rev_link_cost: unsigned } |  |  | {30;1440;0;0;0;10;4;0;0;30;10;1;0;0} | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | adp_net_traversal_time Maximum time that a packet is expected to take to reach any node from any node in seconds Data type: UNSIGNED8 Authorized value: 0 to 255 Default value: 30 adp_routing_table_entry_TTL This parameter defines the time to live in minutes of a routing table entry. Data type: UNSIGNED16 Authorized value: 0 to 65535 Default value: 1440 adp_Kr T A weight factor for the Robust Mode to calculate link cost. Data type: UNSIGNED8 Authorized value: 0 to 31 Default value: 0 adp_Km A weight factor for modulation to calculate link cost. Data type: UNSIGNED8 Authorized value: 0 to 31 Default value: 0 adp_Kc A weight factor for number of active tones to calculate link cost.. Data type: UNSIGNED8 Authorized value: 0 to 31 Default value: 0 adp_Kq A weight factor for LQI to calculate route cost. Data type: UNSIGNED8 Authorized value: 0 to 50 Default value: 10 adp_Kh A weight factor for LQI to calculate route cost. Data type: UNSIGNED8 Authorized value: 0 to 31 Default value: 4 adp_Krt A weight factor for LQI to calculate route cost. Data type: UNSIGNED8 Authorized value: 0 to 31 Default value: 0 adp_RREQ_retries This parameter defines the maximum number of RREQ retransmissions after the RREP reception timeout has been reached. Data type: UNSIGNED8 Authorized value: 0 to 255 Default value: 0 adp_RREQ_ wait This parameter defines the time to wait in seconds between two consecutive RREQ or RLCREQ transmissions. Data type: UNSIGNED8 Authorized value: 0 to 255 Default value: 30 adp_Blacklist_table_entry_TTL This parameter defines the time to live in minutes of blacklisted entry. Data type : UNSIGNED16 Authorized value : 0 to 65535 Default value : 10 adp_unicast_RREQ_gen_enable If TRUE, the RREQ shall be generated with its ''unicast RREQ'' flag set to '1'. If FALSE, the RREQ shall be generated with its ''unicast RREQ'' flag set to '0'. Data type: BOOLEAN Authorized value: 0 : FALSE 1 : TRUE Default value: 1 (TRUE) adp_RLC_enabled Enable the sending of RLCREQ frame by the device Data type : BOOLEAN Authorized value: 0 : FALSE 1 : TRUE Default value : 0 (FALSE) adp_add_rev_link_cost This parameter represents an additional cost to take into account a possible asymmetry in the link. Data type: UNSIGNED8 Authorized value: 0 to 255 Default value: 0
x | x |  |  | 7 | adp_broadcast_log_table_entry_TTL | long_unsigned |  |  | 2 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | This attribute defines the number of minutes below which an entry in the Broadcast Table remains active in the table. On timer expiration, the entry is automatically removed. Data type: UNSIGNED16 Authorized value: 0 to 65535 Default value: 2
x | x |  |  | 8 | adp_routing_table | array[0..150] (routing_table) routing_table: struct { destination_address: long_unsigned next_hop_address: long_unsigned route_cost: long_unsigned hop_count: unsigned weak_link_count: unsigned valid time: long_unsigned } |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | destination_address This attribute provides the short MAC address of the destination. Data type: UNSIGNED16 Authorized value: 0 to 0x7FFF next_hop_address This attribute provides the short MAC address of the next hop of the route towards the destination. Data type: UNSIGNED16 Authorized value: 0x0000 to 0x7FFF route_cost This attribute provides the route cost towards the destination. Data type: UNSIGNED16 Authorized value: 0x0000 to 0xFFFF hop_count This attribute provides the hop count towards the destination. Data type: UNSIGNED8 Authorized value: 0 to 14 weak_link_count Number of weak links on the route Data type: UNSIGNED8 Authorized value: 0 to 14 valid_time This attribute provides the remaining time in minutes until which this entry is considered valid. Data type: UNSIGNED16 Authorized value: 0 – 65535
x | x |  |  | 9 | adp_context_information_table | array[0..16] (context_information_table) context_information_table ::= structure { CID: bit-string, context_length: unsigned, context: octet-string, C: boolean, valid_lifetime: long-unsigned } |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | CID This attribute provides the 4-bit 6LoWPAN context identifier extension field value for the related context. Data type: BITSTRING Authorized value: 0x00 – 0x0F context_length This attribute provides the length of the context in bits. Data type: UNSIGNED8 Authorized value: 0x00 to 0x80 context This attribute provides a 6LoWPAN context. It may be a 64-bit ULA prefix, a multicast context or any other type of information coded on up to 128 bits. The original context information (e.g. transmited over the PLC media) can be retrieved using the context length information. Data type: OCTETSTRING Authorized value: Size = 16 C Indicates if the context is valid for use in compression Data type: BOOLEAN Authorized value: FALSE: only decompression is allowed TRUE: compression and decompression are allowed valid_lifetime This attribute provides the 6LoWPAN context remaining time to live in minutes. Data type: UNSIGNED16 Authorized value: 0 - 65353
x | x |  |  | 10 | adp_blacklist_table | array[0..32] (blacklisted_neighbour_set) blacklisted_neighbour_set ::= structure { blacklisted_neighbour_address: long-unsigned, valid_time: long-unsigned } |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | Blacklisted_neighbour_address This attribute provides the short MAC address of the neighbour blacklisted by LOADng. Data type : UNSIGNED16 Authorized value : 0x0000 to 0x7FFF valid_time Remaining time in minutes until which this entry is considered valid. Data type: UNSIGNED16 Authorized value: 0 to 65535
x | x |  |  | 11 | adp_broadcast_log_table | array[0..32] (broadcast_log_table) broadcast_log_table ::= structure { source_address: long-unsigned, sequence_number: unsigned, valid_time: long-unsigned } |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | source_address This attribute provides the short MAC address of the broadcast initiator. Data type: UNSIGNED16 Authorized value: 0x0000 to 0x7FFF sequence_number This attribute provides the sequence number contained in the 6LoWPAN broadcast header. Data type: UNSIGNED8 Authorized value: 0x00 to 0xFF valid_time Remaining time in minutes until which this entry is considered valid. Data type : UNSIGNED16 Authorized value : 0 to 65535
x | x |  |  | 12 | adp_group_table | array[1..16] (group_address) group_address: long-unsigned |  |  | {0x8001} | -- | -- | Get | Get | -- | -- | Get | Get | The content of this array is directly mapped from the multicast_IPv6 _Adresses attribute, located in the IPv6Setup object, and according to the rule defined in RFC 4944, chapter 9. In any case, the first element of this sequence, initialized with the following default value, shall never be deleted. group_address Group address to which this node has been subscribed. Data type : UNSIGNED16 Authorized value : 0x8000 to 0x9FFF Default value : 1 entry with Group_address = 0x8001
x | x |  |  | 13 | adp_max_join_wait_time | long_unsigned |  |  | 180 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | This parameter indicates the LBP network join timeout in seconds. Data type : UNSIGNED16 Authorized value : 0 to 1023 Default value : 180
x | x |  |  | 14 | adp_path_discovery_time | unsigned |  |  | 40 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | This parameter indicates the timeout for path discovery in seconds. Data type: UNSIGNED8 Authorized value: 0 – 255 Default value: 40
x | x |  |  | 15 | adp_active_key_index | unsigned |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | This parameter defines the index of the active GMK to be used for data transmission. Data type: UNSIGNED8 Authorized value: 0 or 1
x | x |  |  | 16 | adp_metric_type | unsigned |  |  | 0x0F | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | Metric Type to be used for routing purposes Data type: UNSIGNED8 Authorized values: 0x0F - COMPOSITE_METRIC 0x00 - HOP_COUNT Default value : 0x0F
x | x |  |  | 17 | adp_coord_short_address | long_unsigned |  |  | 0x0000 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | This parameter defines the short address of the coordinator. Data type: UNSIGNED16 Authorized value: 0x0000 to 0x7FFF Default value: 0x0000
x | x |  |  | 18 | adp_disable_default_routing | boolean |  |  | 0 | -- | -- | Get | Get | -- | -- | Get | Get | If TRUE, the default routing (LOADng) is disabled. If FALSE, the default routing (LOADng) is enabled. Data type: BOOLEAN Authorized value: FALSE - TRUE Default value: FALSE
x | x |  |  | 19 | adp_device_type | enum |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | adp_device_type This parameter defines the type of the device connected to the modem. Data type: ENUM Authorized value: 0 to 2 0: PAN device 1: PAN coordinator 2: Not Defined Default value: 0
x | x
x | x |  |  |  | AdpLBPAssociationSetup |  | 1 | 0 | 0-0:94.33.14.255 | [8 empty] | This object contains parameters for Bootstrapping procedure setup
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E210EFF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | structure { Association_max_retry: unsigned8 Association_rand_wait_time_step: unsigned8 Association_alt_PAN: boolean Join_LQI_threshold: unsigned8 Active_scan_duration: unsigned8 } |  |  | {8;15;1;52,15} | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | Association_max_retry This attribute indicates the maximum number of association retries carried out for one PAN. Authorized value: 1 to 255 Association_rand_wait_time_step This attribute indicates the waiting window time step in minutes between two associations retries for the same PAN. Authorized value : 0 to 255 Association_alt_PAN This attribute indicates whether or not the device tries to join an alternate PAN after reaching Association_max_retry retries. Authorized value : 0 : FALSE 1 : TRUE Join_LQI_threshold This attribute specifies the LQI threshold value to be used for LBA and PAN selection. Authorized value : 0 to 255 Active_scan_duration This attribute specifies the duration in seconds of the active scan. It is recommended that this attribute is greater than mac_beacon_randomization_window_length. Authorized value : 0 to 255
x | x
x | x |  |  |  | AdpLQIRange |  | 1 | 0 | 0-0:94.33.16.255 | [8 empty] | The LQI range defines the lower and higher LQI value used for the metric computation
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E2110FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | structure { adp_low_LQI_value adp_high_LQI_value } |  |  | {0;255} | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | adp_low_LQI_value The low LQI value defines the lower LQI value used for the metric computation. Data type: UNSIGNED8 Authorized value: 0 to 255 Default value: 0 adp_high_LQI_value The high LQI value defines the higher LQI value used in metric computation. Data type: UNSIGNED8 Authorized value: 0 to 255 Default value: 255
x | x
x | x |  |  |  | AdpRREPWait |  | 1 | 0 | 0-0:94.33.15.255 | [8 empty] | A meter shall wait adp_RREP_Wait seconds between two successive RREP generations
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E210FFF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | unsigned |  |  | 10 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | value adp_RREP_Wait time in seconds Data type: UNSIGNED8 Authorized value: 0 to 255 Default value: 10
x | x
x | x |  |  |  | AdpDefaultCoordRouteEnabled |  | 1 | 0 | 0-0:94.43.135.255 | [8 empty] | Adds a default route to the PAN coordinator after successful completion of the bootstrapping procedure
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E2B87FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | boolean |  |  | FALSE | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | If TRUE, the adaptation layer adds a default route to the coordinator after successful completion of the bootstrapping procedure. If FALSE, no default route (LOADng) will be created. Data type: BOOLEAN Authorized value: FALSE - TRUE Default value: TRUE
x | x
x | x |  |  |  | G3-PLC MAC layer counters |  | 90 | 1 | 0-0:29.0.0.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00001D0000FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | mac_Tx_data_packet_count | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 3 | mac_Rx_data_packet_count | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 4 | mac_Tx_cmd_packet_count | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 5 | mac_Rx_cmd_packet_count | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 6 | mac_CSMA_fail_count | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 7 | mac_CSMA_no_ACK_count | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 8 | mac_bad_CRC_count | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 9 | mac_Tx_data_broadcast_count | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 10 | mac_Rx_data_broadcast_count | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 1 | reset | integer |  |  |  | -- | -- | Action | Action | -- | -- | Action | Action
x | x
x | x |  |  |  | G3-PLC MAC setup |  | 91 | 1 | 0-0:29.1.0.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00001D0100FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | mac_short_address | long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | This attribute defines the 16-bit address that the device uses to communicate through the PAN. Data type: UNSIGNED16 Authorized value : 0x0001 – 0x7FFF : short MAC address allocated by the PAN coordinator during the device registration. 0xFFFE : Indicates that the device has found a PAN coordinator but a valid short MAC address has not yet been allocated. 0xFFFF : Indicates that the device has not found a PAN coordinator.
x | x |  |  | 3 | mac_RC_coord | long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | Route cost to coordinator, to be used in the beacon payload as RC_COORD Data type: UNSIGNED16 Authorized value: 0x0000 – 0xFFFF
x | x |  |  | 4 | mac_PAN_id | long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | The 16-bit identifier of the PAN through which the device is operating. Data type: UNSIGNED16 Authorized value: 0x0000 – 0xFFFE : Gives the PAN identifier on which the device is operating 0xFFFF : Indicates that the device is not currently associated.
x | x |  |  | 5 | mac_key_table | array |  |  |  | -- | -- | -- | -- | -- | -- | -- | -- | GMK key provisioning is only possible by boostrap
x | x |  |  | 6 | mac_frame_counter | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | The outgoing frame counter for this device, used when ciphering frames at MAC layer.
x | x |  |  | 7 | mac_tone_mask | bit_string [72] |  |  | 0xFFFFFFFFF000000000 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | This attribute specifies the list of carriers (one bit = one carrier) to be used during symbol formation. (LSB representing the lowest frequency of the CENELEC or FCC bandplans) For CENELEC A => All carriers ON - 0x000000000FFFFFFFFF => (bit 36 is MSB, bit 71 is LSB of CENELEC-A bandplan) For FCC => All carriers ON - 0xFFFFFFFFFFFFFFFFFF=> (bit 0 is MSB, bit 71 is LSB of FCC bandplan) Data type: BITSTRING Authorized value: size = 72 bits Default value: 0x000000000FFFFFFFFF
x | x |  |  | 8 | mac_TMR_TTL | unsigned |  |  | 2 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | Maximum valid time of tone map parameters in the neighbour table in minutes. Data type: UNSIGNED8 Authorized values: 0 to 255 Default value: 2
x | x |  |  | 9 | mac_max_frame_retries | unsigned |  |  | 5 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | Maximum number of retransmissions. Data type: UNSIGNED8 Authorized values: 0 to 10 Default value: 5
x | x |  |  | 10 | mac_neighbour_table_entry_TTL | unsigned |  |  | 255 | -- | -- | -- | -- | -- | -- | -- | -- | not used any more in Recommendation ITU-T G.9903 (08/2017)
x | x |  |  | 11 | mac_neighbour_table | array[0..75] (neighbour_table_entry) neighbour_table_entry ::= structure { short_address: long-unsigned, payload_modulation_scheme: boolean, tone_map: bit-string, modulation: enum, tx_gain: integer, tx_res: enum, tx_coeff: bit-string, reverse_lqi: unsigned, phase_differential: integer, TMR_valid_time: unsigned, neighbour_valid_time: unsigned } |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | The neighbour table contains information about all the devices within the POS of the device. One element of the table represents one PLC direct neighbour of the device. short_address The MAC Short Address of the node which this entry refers to. Data type: UNSIGNED16 Authorized value: 0x0000 – 0xFFFF payload_modulation_scheme Payload Modulation scheme to be used when transmitting to this neighbour. Data type: BOOLEAN Authorized value: FALSE: Differential TRUE: Coherent tone_map The Tone Map parameter defines which frequency sub-band can be used for communication with the device. A bit set to 1 means that the frequency sub-band can be used, and a bit set to 0 means that frequency sub-band shall not be used. Data type: BITSTRING Bit Spectrum CENELEC-A Authorized value: size = 6 bits => (bit 0.. bit 5) CENELEC-A Tone Map (TM[0]..TM[5]) Bit Spectrum FCC Authorized value: size = 24 bits => (bit 0.. bit 23) FCC Tone Map (TM[0]..TM[23]) modulation The modulation type to use for communicating with the device. Data type: ENUM Authorized value: 0: ROBO 1: DBPSK or BPSK 2: DQPSK or QPSK 3: D8PSK or 8PSK 4: 16-QAM tx_gain This parameter specifies the tx gain (in steps of tx_res) to apply when transmitting to the neighbour. Data type: INTEGER8 Authorized value: 0x00 to 0x0F tx_res This parameter defines the TX Gain resolution corresponding to one gain step. Data type: ENUM Authorized value: 0: 6 dB 1: 3 dB tx_coeff A bitmap to specify the gain for each one of the sub bands when transmitting to the neighbour. CENELEC-A: 4bits per subband - (bit 0) sign: sign for the gain on sub band (“0” = positive gain, “1” = negative gain) - (bit 1 to bit 3) value: gain to apply to the sub band (bit 1 is MSB, bit 3 is LSB) FCC: 2bits per subband - (bit 0) sign: sign for the gain on sub band (“0” = positive gain, “1” = negative gain) - (bit 1) value: gain to apply to the sub band Data type: BITSTRING Bit Spectrum CENELEC-A Authorized value: size = 24 bits => (bit 0.. bit 23) CENELEC A Tone Map (TM[0]..TM[5]) Bit Spectrum FCC Authorized value: size = 48 bits => (bit 0.. bit 47) FCC Tone Map (TM[0]..TM[23]) reverse_lqi Link Quality Indicator (LQI) of the link to the neighbour (reverse LQI). Data type: UNSIGNED8 Authorized value: 0 to 255 phase_differential This parameter provides the phase difference between the AC phase of the local node and the neighbour node Data type : integer Authorized value : 0: neighbour node and local node are in phase 1: local node leads neighbour node by 60 degrees 2: local node leads neighbour node by 120 degrees 3: neighbour node and local node are in phase opposition 4: neighbour node leads local node by 120 degrees 5: neighbour node leads local node by 60 degrees TMR_valid_time Remaining time in minutes until which the contents of the neighbour table are considered valid. Each time an entry of the neighbour table is created or updated, this field is set to mac_TMR_TTL. Data type: UNSIGNED8 Authorized value: 0 to 255 neighbour_valid_time not used any more in Recommendation ITU-T G.9903 (08/2017) To ensure compliancy to the DLMS Blue Book class id 91 v1 , the field TMR_valid_time is placed here again. Data type: UNSIGNED8 Authorized value: 0 to 255
x | x |  |  | 12 | mac_high_priority_window_size | unsigned |  |  | 7 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | This attribute defines the high priority contention window size in number of slots. Data type: UNSIGNED8 Authorized values: 1 to 7 Default value: 7
x | x |  |  | 13 | mac_CSMA_fairness_limit | unsigned |  |  | 25 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | This attribute specifies how many failed back-off attempts, back-off exponent is set to minBE. Data type: UNSIGNED8 Authorized values: 2*(mac_max_BE – mac_min_BE) to 255 Default value: 25
x | x |  |  | 14 | mac_beacon_randomization_window_length | unsigned |  |  | 12 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | Duration time in seconds for the beacon randomization. Data type: UNSIGNED8 Authorized values: 1 to 254 Default value: 12
x | x |  |  | 15 | mac_A | unsigned |  |  | 8 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | This parameter controls the adaptive CW linear decrease. Data type: UNSIGNED8 Authorized values: 3 to 20 Default value: 8
x | x |  |  | 16 | mac_K | unsigned |  |  | 5 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | Rate Adaptation factor for channel access fairness limit. Data type: UNSIGNED8 Authorized values: 1 to mac_CSMA_fairness_limit Default value: 5
x | x |  |  | 17 | mac_min_CW_attempts | unsigned |  |  | 10 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | Number of consecutive attempts while using minimum CW. Data type: UNSIGNED8 Authorized values: 0 to 255 Default value: 10
x | x |  |  | 18 | mac_cenelec_legacy_mode | unsigned |  |  | 1 | -- | -- | Get | Get | -- | -- | Get | Get | This read only attribute indicates the capability of the node. 0: The following configuration is used (legacy mode): • Elementary interleaving • Interleaver parameters n_i and n_j are not swapped when I(i,j) = 0 1: The following configuration is used (non legacy mode): • Full Block interleaving • Interleaver parameters n_i and n_j are swapped when I(i,j) = 0 Data type: UNSIGNED8 Authorized values: 1
x | x |  |  | 19 | mac_FCC_legacy_mode | unsigned |  |  | 1 | -- | -- | Get | Get | -- | -- | Get | Get | This read only attribute indicates the capability of the node. 0: The following configuration is used (legacy mode): • Differential FCH modulation; • Elementary interleaving; • Interleaver parameters n_i and n_j are not swapped when I(i,j) = 0; • Single RS block. 1: The following configuration is used (non legacy mode): • Coherent FCH modulation; • Full Block interleaving; • Interleaver parameters n_i and n_j are swapped when I(i,j) = 0; • Two RS blocks. Data type: UNSIGNED8 Authorized values: 1
x | x |  |  | 20 | mac_max_BE | unsigned |  |  | 8 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | Maximum value of backoff exponent. Data type: UNSIGNED8 Authorized values: mac_Min_BE to 20 Default value: 8
x | x |  |  | 21 | mac_max_CSMA_backoffs | unsigned |  |  | 50 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | Maximum number of backoff attempts. Data type: UNSIGNED8 Authorized values: 0 to 255 Default value: 50
x | x |  |  | 22 | mac_min_BE | unsigned |  |  | 3 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | Minimum value of backoff exponent. Data type: UNSIGNED8 Authorized values: 0 to 20 Default value: 3
x | x |  |  | 1 | mac_get_neighbour_table_entry | long_unsigned |  |  |  | -- | -- | Action | Action | -- | -- | Action | Action | This method is used to retrieve the mac neighbour table for one MAC short address. It may be used to perform topology monitoring by the client. The description of the data returned by the method follows exactly the same format as the neighbour table entries described before. Request parameter: mac_short_address Data type: UNSIGNED16
x | x
x | x |  |  |  | MacCoherentTransmission |  | 1 | 0 | 0-0:94.33.12.255 | [8 empty] | Indicates the coherent modulation scheme to set in the tone map response
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E210CFF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | enum |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | value Data type: ENUMERATED Authorized values: 0 only differential modulation scheme shall be set in tone map response 1 only coherent modulations scheme shall be set in tone map response 2 Either coherent or differential scheme may be set in tone map response. Default value: 0
x | x
x | x |  |  |  | MacDeviceTable |  | 1 | 0 | 0-0:94.33.13.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E210DFF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | array[250] (mac_device) mac_device ::= structure { PANId Short_address Frame_counter } |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | PANId The PANId of the device. Data type: UNSIGNED16 Authorized values: 0x0000 to 0xFFFF Short_address The 16-bit short address of the device. Data type: UNSIGNED16 Authorized values: 0x0000 to 0x7FFF Frame_counter The incoming 32-bit frame counter of the device. Data type: UNSIGNED32 Authorized values: 0x00000000 to 0xFFFFFFFFF
x | x
x | x |  |  |  | MacPOSTableEntryTTL |  | 1 | 0 | 0-0:94.43.136.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E2B88FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | unsigned |  |  | 255 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | Maximum valid Ttime to live for an entry in the POSneighbour table in minutes. Data type: UNSIGNED8 Authorized values: 0 to 255 Default value: 255
x | x
x | x |  |  |  | MacPOSTable |  | 1 | 0 | 0-0:94.43.137.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E2B89FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | array [0..250] (POS_entry) POS_entry ::= structure { short_address: long_unsigned foward_lqi: unsigned POS_valid_time: unsigned } |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | The POS table contains information about devices in the POS of the device. short_address The MAC Short Address of the node which this entry refers to. Data type: UNSIGNED16 Authorized value: 0x0000 – 0xFFFF foward_lqi Link Quality Indicator (LQI) of the link from the neighbour (foward LQI). Data type: UNSIGNED8 Authorized value: 0 to 255 POS_valid_time Remaining time in minutes until which this entry in the POS table is considered valid. Every time an entry is created or a frame (data or ACK) is received from this neighbour, it is set to POS_table_entry_TTL. When it reaches zero, this entry is no longer valid in the table and may be removed. Data type: UNSIGNED8 Authorized value: 0 to 255
x | x
x | x |  |  |  | MacBroadcastMaxCWEnabled |  | 1 | 0 | 0-0:94.43.138.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E2B8AFF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | boolean |  |  | TRUE | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | If enabled, MAC uses maximum contention window for broadcast frames. Data type: BOOLEAN Authorized values: FALSE-TRUE Default value: TRUE
x | x
x | x |  |  |  | MacTransmitAtten |  | 1 | 0 | 0-0:94.43.139.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E2B8BFF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | unsigned |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | Attenuation of the output level in dB. Data type: UNSIGNED8 Authorized values: 0 to 25 Default value: 0
x | x
x | x |  |  |  | InitiatorElectricalPhase |  | 1 | 0 | 0-0:96.62.0.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "0000603E00FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | enum |  |  | 0 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | This attribute is written by the client system to indicate the phase number to which the client is connected. The local node (meter) must not modify the value of this parameter. Only the DLMS/COSEM client may modify this parameter. value Data type: ENUMERATED Authorized values: 0: Not defined 1: Phase 1 2: Phase 2 3: Phase 3 Default value : 0 (Not defined)
x | x
x | x |  |  |  | DeltaElectricalPhase |  | 1 | 0 | 0-0:96.62.1.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "0000603E01FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | enum |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | This attribute indicates the phase difference between the client system's connecting phase and the meter's connecting phase. The meter uses the information available from the G3-PLC layer. Enumerated description: 0 = Not defined, 1 = The meter is connected to the same phase as the client system, 2 = The phase difference between the meter's connecting phase and the client system's connecting phase is equal to 60 degrees, 3 = The phase difference between the meter's connecting phase and the client system's connecting phase is equal to 120 degrees, 4 = The phase difference between the meterr's connecting phase and the client system's connecting phase is equal to 180 degrees, 5 = The phase difference between the meter's connecting phase and the client system's connecting phase is equal to -120 degrees, 6 = The phase difference between the meter's connecting phase and the client system's connecting phase is equal to -60 degrees. Data type: ENUMERATED Authorized values: 0: Not defined 1: 0 degree 2: 60 degrees 3: 120 degrees 4: 180 degrees 5: -120 degrees 6: -60 degrees
x | x
x | x |  |  |  | AlternatePANId |  | 1 | 0 | 0-0:94.33.55.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E2137FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | This data contains the alternate PAN Id that has been indicated by the MLME-COMM-STATUS.indication with Status = ALTERNATE_PANID_DETECTION. value Data type: UNSIGNED16 Authorized value: 0 to 65535
x | x
x | x |  |  |  | AlternatePANIdLog |  | 7 | 1 | 0-0:94.33.9.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E2109FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | buffer | array |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | selective access per range and entry
x | x |  |  | 3 | capture_objects | array[1..*](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:94.33.55.255,2,0},} | -- | -- | Get | Get | -- | -- | Get | Get | clock;PANid
x | x |  |  | 4 | capture_period | double_long_unsigned |  |  | 0 | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 5 | sort_method | enum |  |  | 1 | -- | -- | Get | Get | -- | -- | Get | Get | unsorted (FIFO)
x | x |  |  | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | -- | Get | Get | -- | -- | Get | Get | unsorted
x | x |  |  | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 8 | profile_entries | double_long_unsigned |  |  | [5..*] | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 1 | reset | integer |  |  |  | -- |  | -- | Action | -- | -- | Action Req S, Res - | Action Req S, Res -
x | x |  |  | 2 | capture |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x
x | x |  |  |  | PAN connection status |  | 1 | 0 | 0-0:94.43.131.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E2B83FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | value | PAN_connection_status ::= structure { routing_table_entry ::= structure; neighbour_table_entry ::= structure } routing_table ::= structure { destination_address: long-unsigned, next_hop_address: long-unsigned, route_cost: long-unsigned, hop_count: unsigned, weak_link_count: unsigned, valid_time: long-unsigned } neighbour_table ::= structure { short_address: long-unsigned, payload_modulation_scheme: boolean, tone_map: bit-string, modulation: enum, tx_gain: integer, tx_res: enum, tx_coeff: bit-string, reverse_lqi: unsigned, phase_differential integer, TMR_valid_time: unsigned, neighbour_valid_time: unsigned } |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | This object contains the network status information for the connection of the end device to the PAN coordinator. The connection status information is based on the - Routing table entry of the ‘PAN coordinator’ and - Neighbour table entry of the ‘Next Hop’
x | x
x | x |  |  |  | PAN connection status profile |  | 7 | 1 | 0-0:94.43.132.255
x | x |  |  | 1 | logical_name | octet_string[6] |  |  | "00005E2B84FF" | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 2 | buffer | array |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get | selective access per range and entry
x | x |  |  | 3 | capture_objects | array[1..*](capture_object_definition) |  |  | {{8,0-0:1.0.0.255,2,0}, {1,0-0:94.43.131.255,2,0},} | -- | -- | Get | Get | -- | -- | Get | Get | clock;PANid
x | x |  |  | 4 | capture_period | double_long_unsigned |  |  | 3600 | -- | -- | Get, Set | Get, Set | -- | -- | Get, Set | Get, Set | allowed range 1,5,10,15,60 min or daily is recommended. default 60 minutes (3600 seconds)
x | x |  |  | 5 | sort_method | enum |  |  | 1 | -- | -- | Get | Get | -- | -- | Get | Get | unsorted (FIFO)
x | x |  |  | 6 | sort_object | capture_object_definition |  |  | {*,*-*:*.*.*.*,*,*} | -- | -- | Get | Get | -- | -- | Get | Get | unsorted
x | x |  |  | 7 | entries_in_use | double_long_unsigned |  |  |  | -- | -- | Get | Get | -- | -- | Get | Get
x | x |  |  | 8 | profile_entries | double_long_unsigned |  |  | [168 ..*] | -- | -- | Get | Get | -- | -- | Get | Get | 7 days with hourly entries, 3 captured objects (min. 168 entries)
x | x |  |  | 1 | reset | integer |  |  |  | -- | -- | -- | Action | -- | -- | Action Req S, Res - | Action Req S, Res -
x | x |  |  | 2 | capture |  |  |  |  | -- | -- | -- | -- | -- | -- | -- | --
x | x

## Access Right Mapping
ATTRIBUTES Access rights according attribute access_mode A= authenticated; E= encrypted S= sigend |  | METHODS Access rights according method access_mode A= authenticated; E= encrypted S= sigend
(0) read-access, (1) write-access, (2) authenticated request [A], (3) encrypted request, (4) digitally signed request, (5) authenticated response, (6) encrypted response, (7) digitally signed response | -- | (0) access, (1) not-used, (2) authenticated request, (3) encrypted request, (4) digitally signed request, (5) authenticated response, (6) encrypted response, (7) digitally signed response | --
(0) read-access, (1) write-access, (2) authenticated request, (3) encrypted request, (4) digitally signed request, (5) authenticated response, (6) encrypted response, (7) digitally signed response | Get | (0) access, (1) not-used, (2) authenticated request, (3) encrypted request, (4) digitally signed request, (5) authenticated response, (6) encrypted response, (7) digitally signed response | Action
(0) read-access, (1) write-access, (2) authenticated request, (3) encrypted request, (4) digitally signed request, (5) authenticated response, (6) encrypted response, (7) digitally signed response | Get, Set | (0) access, (1) not-used, (2) authenticated request, (3) encrypted request, (4) digitally signed request, (5) authenticated response, (6) encrypted response, (7) digitally signed response | Action Req S, Res -
(0) read-access, (1) write-access, (2) authenticated request, (3) encrypted request, (4) digitally signed request, (5) authenticated response, (6) encrypted response, (7) digitally signed response | Set
(0) read-access, (1) write-access, (2) authenticated request, (3) encrypted request, (4) digitally signed request, (5) authenticated response, (6) encrypted response, (7) digitally signed response | Get Req S , Res -
(0) read-access, (1) write-access, (2) authenticated request, (3) encrypted request, (4) digitally signed request, (5) authenticated response, (6) encrypted response, (7) digitally signed response | Get, Set Req S, Res -
(0) read-access, (1) write-access, (2) authenticated request, (3) encrypted request, (4) digitally signed request, (5) authenticated response, (6) encrypted response, (7) digitally signed response | Set Req S, Res -

## Generic Events
Event Code | Name | Description | Standard Event Log | Fraud Detection Log | Disconnector Control Log | Power Quality Event Log | Communication Session Log | M-Bus Event Log | M-Bus Control Log 1 | M-Bus Control Log 2 | M-Bus Control Log 3 | M-Bus Control Log 4 | Security Event Log | Certification Protected Log | Mandatory/optional/NA
1 | Power Down | Indicates a complete power down of the device. Please note that this is related to the device and not necessarily to the network. | x | [9 empty] | x |  | M
2 | Power Up | Indicates that the device is powered again after a complete power down. | x | [9 empty] | x |  | M
3 | Daylight saving time enabled or disabled | Indicates the regular change from and to daylight saving time. The time stamp shows the time before the change. This event is not set in case of manual clock changes and in case of power failures. | x | [11 empty] | M
4 | Clock adjusted (old date/time) | Indicates that the clock has been adjusted. The date/time that is stored in the event log is the old date/time before adjusting the clock. | x | [9 empty] | x |  | M
5 | Clock adjusted (new date/time) | Indicates that the clock has been adjusted. The date/time that is stored in the event log is the new date/time after adjusting the clock. | x | [9 empty] | x |  | M
6 | Clock invalid | Indicates that clock may be invalid, i.e. if the power reserve of the clock has exhausted. It is set at power up. | x | [11 empty] | M
7 | Replace Battery | Indicates that the battery must be exchanged due to the expected end of life time. | x | [11 empty] | O
8 | Battery voltage low | Indicates that the current battery voltage is low. | x | [11 empty] | O
9 | TOU - activity calendar activated | Indicates that the passive structure of the TOU activity calendar has been activated. | x | [11 empty] | M
10 | Error register cleared | Indicates that the error register was cleared. | x | [9 empty] | x |  | M
11 | Alarm register cleared | Indicates that the alarm register was cleared. | x | [9 empty] | x |  | M
12 | Program memory error | Indicates a physical or a logical error in the program memory. | x | [9 empty] | x |  | M
13 | RAM error | Indicates a physical or a logical error in the RAM. | x | [9 empty] | x |  | M
14 | NV memory error | Indicates a physical or a logical error in the non volatile memory | x | [9 empty] | x |  | M
15 | Watchdog error | Indicates a watch dog reset or a hardware reset of the microcontroller. | x | [9 empty] | x |  | M
16 | Measurement system error | Indicates a fatal logical or physical error in the measurement system and/or the legally relevant part of the measurement instrument which causes the device certification to be cancelled. | x | [9 empty] | x |  | M
17 | Firmware ready for activation | Indicates that the new firmware has been successfully downloaded and verified, i.e. it is ready for activation *depending on LR or NLR firmware image the event must be recoded only in the appropriate log | x* | [9 empty] | x | x* | M
18 | Firmware activated | Indicates that a new firmware has been activated *depending on LR or NLR firmware image the event must be recoded only in the appropriate log | x* | [9 empty] | x | x* | M
19 | TOU - passive activity calendar programmed | Indicates that the passive structure or a new activation date/time of the TOU activity calendar were programed | x | [11 empty] | M
20 | External alert detected | Indicates signal detected on the meter's input terminal | x | [11 empty] | NA
21 | End of non-periodic billing interval | Indicates the end of an non-periodic billing interval (asynchronous billing) | x | [11 empty] | M
22 | Capturing of load profile 1 enabled | Indicates capturing of load profile 1 has started | x | [11 empty] | M
23 | Capturing of load profile 1 disabled | Indicates capturing of load profile 1 has ended | x | [11 empty] | M
24 | Capturing of load profile 2 enabled | Indicates capturing of load profile 2 has started | x | [11 empty] | M
25 | Capturing of load profile 2 disabled | Indicates capturing of load profile 2 has ended | x | [11 empty] | M
26 | Communication started on remote interface LAN/WAN | Indicates that the communication was started on the remote interface LAN/WAN |  |  |  |  | x | [5 empty] | x |  | M
27 | Communication ended on remote interface LAN/WAN | Indicates that the communication has ended on the remote interface LAN/WAN |  |  |  |  | x | [5 empty] | x |  | M
28 | Communication started on local interface WZ | Indicates that the communication was started on the locale interface WZ |  |  |  |  | x | [5 empty] | x |  | M
29 | Communication ended on local interface WZ | Indicates that the communication has ended on the local interface WZ |  |  |  |  | x | [5 empty] | x |  | M
30 | FOTA upgrading initial | Indicates FOTA upgrading has been started. | x
31 | FOTA upgrading successfully | Indicates FOTA upgrading is finished successfully. | x
32 | FOTA upgrading failed | Indicates FOTA upgrading is failed. | x
33 | reserved for future use
34 | reserved for future use
35 | reserved for future use
36 | reserved for future use
37 | reserved for future use
38 | reserved for future use
39 | reserved for future use
40 | Terminal cover removed | Indicates that the terminal cover has been removed. |  | x | [8 empty] | x |  | M
41 | Terminal cover closed | Indicates that the terminal cover has been closed. |  | x | [8 empty] | x |  | M
42 | Strong DC field detected | Indicates that a strong magnetic DC field has been detected. |  | x | [8 empty] | x |  | M
43 | No strong DC field anymore | Indicates that the strong magnetic DC field has disappeared. |  | x | [8 empty] | x |  | M
44 | Meter cover removed | Indicates that the meter cover has been removed. |  | x | [8 empty] | x |  | M
45 | Meter cover closed | Indicates that the meter cover has been closed. |  | x | [8 empty] | x |  | M
46 | Association authentication failure | Indicates that a user tried to gain access with wrong credentials (intrusion detection) or HLS access challenge processing failed |  | x | [8 empty] | x |  | M
47 | One or more parameters changed | Indicates the detection of a SET or ACTION access to an attribute or method for re-configuration purposes | x | [11 empty] | M
48 | Global key(s) changed | One or more global keys changed | x | [9 empty] | x |  | M
49 | Decryption or authentication failure | Decryption with currently valid key (global or dedicated) failed to generate a valid APDU or authentication tag |  | x | [8 empty] | x |  | M
50 | Replay attack | Receive frame counter value less or equal to the last successfully received frame counter in the received APDU Event signalizes as well the situation when the DC has lost the frame counter synchronization. |  | x | [8 empty] | x |  | M
51 | FW verification/activation failed | Indicates the transferred firmware verification failed i.e. cannot be activated. *depending on LR or NLR firmware image the event must be recoded only in the appropriate log | x* | [9 empty] | x | x* | M
52 | Unexpected consumption | Indicates consumption is detected at least on one phase when the disconnector has been disconnected | x | [11 empty] | O
53 | Re-initialisation of the RNG | Re-initialisation of the random number generator |  | x | [8 empty] | x |  | M
54 | Local interface de-activated | Indicates the de-activation of the local interface for a time period due to failed association attempts (event code 46) or remote command |  | x | [8 empty] | x |  | M
55 | Local interface re-activated | Indicates the re-activation of the local interface after a time period due to failed association attempts (event code 46) or remote command |  | x | [8 empty] | x |  | M
56 | Tariffication scheme change | indicates a change from 'central' tariffication to 'rated' certification or viceversa | x | [11 empty] | M
57 | Start Certification mode | Indicates the activation of the certification mode. | x | [11 empty] | M
58 | End Certification mode | Indicates the end of the certification mode either by command or time-out. | x | [11 empty] | M
59 | Disconnector ready for manual reconnection | Indicates that the disconnector has been set into the Ready_for_reconnection state and can be manually reconnected |  |  | x | [7 empty] | x |  | M
60 | Manual disconnection | Indicates that the disconnector has been manually disconnected. |  |  | x | [7 empty] | x |  | M
61 | Manual connection | Indicates that the disconnector has been manually connected. |  |  | x | [7 empty] | x |  | M
62 | Remote disconnection | Indicates that the disconnector has been remotely disconnected. |  |  | x | [7 empty] | x |  | M
63 | Remote connection | Indicates that the disconnector has been remotely connected. |  |  | x | [7 empty] | x |  | M
64 | Local disconnection | Indicates that the disconnector has been locally disconnected (i.e. via the limiter or current supervision monitors). |  |  | x | [7 empty] | x |  | M
65 | Limiter threshold exceeded | Indicates that the limiter threshold has been exceeded. |  |  | x | [7 empty] | x |  | M
66 | Limiter threshold ok | Indicates that the monitored value of the limiter dropped below the threshold. |  |  | x | [7 empty] | x |  | M
67 | Limiter threshold config changed | Indicates that the limiter threshold configuration (threshold value; integration time) has been changed |  |  | x | [7 empty] | x |  | M
68 | Disconnect/Reconnect failure | Indicates that the a failure of disconnection or reconnection has happened (control state does not match output state) |  |  | x | [7 empty] | x |  | M
69 | Local reconnection | Indicates that the disconnector has been locally re-connected (i.e. via the limiter or current supervision monitors). |  |  | x | [7 empty] | x |  | M
70 | Supervision monitor 1 threshold exceeded | Indicates that the supervision monitor threshold has been exceeded. |  |  | x | [9 empty] | NA
71 | Supervision monitor 1 threshold ok | Indicates that the monitored value dropped below the threshold. |  |  | x | [9 empty] | NA
72 | Supervision monitor 2 threshold exceeded | Indicates that the supervision monitor threshold has been exceeded. |  |  | x | [9 empty] | NA
73 | Supervision monitor 2 threshold ok | Indicates that the monitored value dropped below the threshold. |  |  | x | [9 empty] | NA
74 | Supervision monitor 3 threshold exceeded | Indicates that the supervision monitor threshold has been exceeded. |  |  | x | [9 empty] | NA
75 | Supervision monitor 3 threshold ok | Indicates that the monitored value dropped below the threshold. |  |  | x | [9 empty] | NA
76 | Undervoltage L1 | Indicates undervoltage on at least L1 phase was detected. |  |  |  | x | [8 empty] | M
77 | Undervoltage L2 | Indicates undervoltage on at least L2 phase was detected. |  |  |  | x | [8 empty] | M
78 | Undervoltage L3 | Indicates undervoltage on at least L3 phase was detected. |  |  |  | x | [8 empty] | M
79 | Overvoltage L1 | Indicates overvoltage on at least L1 phase was detected. |  |  |  | x | [8 empty] | M
80 | Overvoltage L2 | Indicates overvoltage on at least L2 phase was detected. |  |  |  | x | [8 empty] | M
81 | Overvoltage L3 | Indicates overvoltage on at least L3 phase was detected. |  |  |  | x | [8 empty] | M
82 | Missing voltage L1 | Indicates that the voltage on at least L1 phase has fallen below the Umin threshold for longer than the time delay. |  |  |  | x | [8 empty] | M
83 | Missing voltage L2 | Indicates that the voltage on at least L2 phase has fallen below the Umin threshold for longer than the time delay. |  |  |  | x | [8 empty] | M
84 | Missing voltage L3 | Indicates that the voltage on at least L3 phase has fallen below the Umin threshold for longer than the time delay. |  |  |  | x | [8 empty] | M
85 | Voltage L1 normal | Indicates that the mains voltage is in normal limits again, e.g. after overvoltage. |  |  |  | x | [8 empty] | M
86 | Voltage L2 normal | Indicates that the mains voltage is in normal limits again, e.g. after overvoltage. |  |  |  | x | [8 empty] | M
87 | Voltage L3 normal | Indicates that the mains voltage is in normal limits again, e.g. after overvoltage. |  |  |  | x | [8 empty] | M
88 | Phase sequence reversal | Indicates wrong mains connection. Usually indicates fraud or wrong installation. For poly phase connection only! | x | [11 empty] | M
89 | Missing neutral | Indicates that the neutral connection from the supplier to the meter is interrupted (but the neutral connection to the load prevails). The phase voltages measured by the meter may differ from their nominal values | x | [11 empty] | O
90 | Phase Asymmetry | Indicates phase asymmetry due to large unbalance of loads connected |  |  |  | x | [8 empty] | O
91 | Current Reversal | Indicates unexpected energy export (for devices which are configured for energy import measurement only) |  | x | [10 empty] | O
92 | Bad Voltage Quality L1 | Indicates that the voltage of L1 does NOT fulfill the following condition: during each period of one week 95 % of the 10 min mean r.m.s, values of the supply voltage are within the range of Un+/- 10 % and all 10 mín mean r.m.s. values of the supply voltage shall be within the range of Un + 10%/- 15%. (acc. EN50160:2010, section 4.2.2) |  |  |  | x | [8 empty] | O
93 | Bad Voltage Quality L2 | Indicates that the voltage of L2 does NOT fulfill the following condition: during each period of one week 95 % of the 10 min mean r.m.s, values of the supply voltage are within the range of Un+/- 10 % and all 10 mín mean r.m.s. values of the supply voltage shall be within the range of Un + 10%/- 15%. (acc. EN50160:2010, section 4.2.2) |  |  |  | x | [8 empty] | O
94 | Bad Voltage Quality L3 | Indicates that the voltage of L3 does NOT fulfill the following condition: during each period of one week 95 % of the 10 min mean r.m.s, values of the supply voltage are within the range of Un+/- 10 % and all 10 mín mean r.m.s. values of the supply voltage shall be within the range of Un + 10%/- 15%. (acc. EN50160:2010, section 4.2.2) |  |  |  | x | [8 empty] | O
95 | Disconnector control - passive activity calendar activated | Indicates that the passive structure of the Disconnector Control activity calendar has been activated. |  |  | x | [7 empty] | x |  | M
96 | Disconnector control - activity calendar programmed | Indicates that the passive structure or a new activation date/time of the Disconnector Control activity calendar were programed |  |  | x | [7 empty] | x |  | M
97 | Load Management - passive activity calendar activated | Indicates that the passive structure of the Load Management activity calendar has been activated. | x | [11 empty] | M
98 | Load Management - activity calendar programmed | Indicates that the passive structure or a new activation date/time of the Load Management activity calendar were programed | x | [11 empty] | M
99 | Consumer message update | Indicates a change in the consumer message code on the meter display, either by remote command or manual message acknowledgement by pressing the button | x | [9 empty] | x |  | M
100 | Communication error M-Bus channel 1 | Indicates a communication problem when reading the meter connected to channel 1 of the M-Bus | [5 empty] | x | [6 empty] | M
101 | Communication ok M-Bus channel 1 | Indicates that the communication with the M-Bus meter connected to channel 1 of the M-Bus is ok again. | [5 empty] | x | [6 empty] | M
102 | Replace Battery M-Bus channel 1 | Indicates that the battery must be exchanged due to the expected end of life time. (Power low - flag from M-Bus device status) | [5 empty] | x | [6 empty] | M
103 | Fraud attempt M-Bus channel 1 | Indicates that a fraud attempt has been registered. (Fraud attempt registered - flag from M-Bus device status) | [5 empty] | x |  |  |  |  | x |  | M
104 | Clock adjusted M-Bus channel 1 | Indicates that the clock has been adjusted. | [5 empty] | x |  |  |  |  | x |  | M
105 | New M-Bus device installed channel 1 | Indicated the meter (M-Bus master) has registered a M-Bus device connected to channel 1 with a new serial number | [5 empty] | x |  |  |  |  | x |  | M
106 | Permanent Error M-Bus channel 1 | Severe error reported by M-Bus device (Permanent error - flag from M-Bus device status) | [5 empty] | x |  |  |  |  | x |  | M
107 | reserved for future use
108 | reserved for future use
109 | Key(s) changed - M-Bus channel 1 | One or more global keys changed for M-Bus device | [5 empty] | x |  |  |  |  | x |  | M
110 | Communication error M-bus channel 2 | Indicates a communication problem when reading the meter connected to channel 2 of the M-Bus | [5 empty] | x | [6 empty] | M
111 | Communication ok M-bus channel 2 | Indicates that the communication with the M-Bus meter connected to channel 2 of the M-Bus is ok again. | [5 empty] | x | [6 empty] | M
112 | Replace Battery M-Bus channel 2 | Indicates that the battery must be exchanged due to the expected end of life time. (Power low - flag from M-Bus device status) | [5 empty] | x | [6 empty] | M
113 | Fraud attempt M-Bus channel 2 | Indicates that a fraud attempt has been registered. (Fraud attempt registered - flag from M-Bus device status) | [5 empty] | x |  |  |  |  | x |  | M
114 | Clock adjusted M-Bus channel 2 | Indicates that the clock has been adjusted. | [5 empty] | x |  |  |  |  | x |  | M
115 | New M-Bus device installed channel 2 | Indicated the meter (M-Bus master) has registered a M-Bus device connected to channel 2 with a new serial number | [5 empty] | x |  |  |  |  | x |  | M
116 | Permanent Error M-Bus channel 2 | Severe error reported by M-Bus device (Permanent error - flag from M-Bus device status) | [5 empty] | x |  |  |  |  | x |  | M
117 | reserved for future use
118 | reserved for future use
119 | Key(s) changed - M-Bus channel 2 | One or more global keys changed for M-Bus device | [5 empty] | x |  |  |  |  | x |  | M
120 | Communication error M-bus channel 3 | Indicates a communication problem when reading the meter connected to channel 3 of the M-Bus | [5 empty] | x | [6 empty] | M
121 | Communication ok M-bus channel 3 | Indicates that the communication with the M-Bus meter connected to channel 3 of the M-Bus is ok again. | [5 empty] | x | [6 empty] | M
122 | Replace Battery M-Bus channel 3 | Indicates that the battery must be exchanged due to the expected end of life time. (Power low - flag from M-Bus device status) | [5 empty] | x | [6 empty] | M
123 | Fraud attempt M-Bus channel 3 | Indicates that a fraud attempt has been registered. (Fraud attempt registered - flag from M-Bus device status) | [5 empty] | x |  |  |  |  | x |  | M
124 | Clock adjusted M-Bus channel 3 | Indicates that the clock has been adjusted. | [5 empty] | x |  |  |  |  | x |  | M
125 | New M-Bus device installed channel 3 | Indicated the meter (M-Bus master) has registered a M-Bus device connected to channel 3 with a new serial number | [5 empty] | x |  |  |  |  | x |  | M
126 | Permanent Error M-Bus channel 3 | Severe error reported by M-Bus device (Permanent error - flag from M-Bus device status) | [5 empty] | x |  |  |  |  | x |  | M
127 | reserved for future use
128 | reserved for future use
129 | Key(s) changed - M-Bus channel 3 | One or more global keys changed for M-Bus device | [5 empty] | x |  |  |  |  | x |  | M
130 | Communication error M-bus channel 4 | Indicates a communication problem when reading the meter connected to channel 4 of the M-Bus | [5 empty] | x | [6 empty] | M
131 | Communication ok M-bus channel 4 | Indicates that the communication with the M-Bus meter connected to channel 4 of the M-Bus is ok again. | [5 empty] | x | [6 empty] | M
132 | Replace Battery M-Bus channel 4 | Indicates that the battery must be exchanged due to the expected end of life time. (Power low - flag from M-Bus device status) | [5 empty] | x | [6 empty] | M
133 | Fraud attempt M-Bus channel 4 | Indicates that a fraud attempt has been registered. (Fraud attempt registered - flag from M-Bus device status) | [5 empty] | x |  |  |  |  | x |  | M
134 | Clock adjusted M-Bus channel 4 | Indicates that the clock has been adjusted. | [5 empty] | x |  |  |  |  | x |  | M
135 | New M-Bus device installed channel 4 | Indicated the meter (M-Bus master) has registered a M-Bus device connected to channel 4 with a new serial number | [5 empty] | x |  |  |  |  | x |  | M
136 | Permanent Error M-Bus channel 4 | Severe error reported by M-Bus device (Permanent error - flag from M-Bus device status) | [5 empty] | x |  |  |  |  | x |  | M
137 | reserved for future use
138 | reserved for future use
139 | Key(s) changed - M-Bus channel 4 | One or more global keys changed for M-Bus device | [5 empty] | x |  |  |  |  | x |  | M
140 | reserved for future use
141 | reserved for future use
142 | reserved for future use
143 | reserved for future use
144 | reserved for future use
145 | reserved for future use
146 | reserved for future use
147 | reserved for future use
148 | reserved for future use
149 | reserved for future use
150 | reserved for future use
151 | reserved for future use
152 | reserved for future use
153 | reserved for future use
154 | reserved for future use
155 | reserved for future use
156 | reserved for future use
157 | reserved for future use
158 | reserved for future use
159 | reserved for future use
160 | Manual disconnection M-Bus channel 1 | Indicates that the disconnector has been manually disconnected. | [6 empty] | x | [5 empty] | O
161 | Manual connection M-Bus channel 1 | Indicates that the disconnector has been manually connected. | [6 empty] | x | [5 empty] | O
162 | Remote disconnection M-Bus channel 1 | Indicates that the disconnector has been remotely disconnected. | [6 empty] | x | [5 empty] | M
163 | Remote connection M-Bus channel 1 | Indicates that the disconnector has been remotely connected. | [6 empty] | x | [5 empty] | M
164 | Valve alarm M-Bus channel 1 | Indicates that a valve alarm has been registered. (Valve Alarm registered - flag from M-Bus device status) | [6 empty] | x | [5 empty] | O
165 | Local disconnection M-Bus channel 1 | Indicates that the disconnector has been locally disconnected. | [6 empty] | x | [5 empty] | M
166 | Local connection M-Bus channel 1 | Indicates that the disconnector has been locally connected. | [6 empty] | x | [5 empty] | M
167 | reserved for future use
168 | reserved for future use
169 | reserved for future use
170 | Manual disconnection M-Bus channel 2 | Indicates that the disconnector has been manually disconnected. | [7 empty] | x |  |  |  |  | O
171 | Manual connection M-Bus channel 2 | Indicates that the disconnector has been manually connected. | [7 empty] | x |  |  |  |  | O
172 | Remote disconnection M-Bus channel 2 | Indicates that the disconnector has been remotely disconnected. | [7 empty] | x |  |  |  |  | M
173 | Remote connection M-Bus channel 2 | Indicates that the disconnector has been remotely connected. | [7 empty] | x |  |  |  |  | M
174 | Valve alarm M-Bus channel 2 | Indicates that a valve alarm has been registered. (Valve Alarm registered - flag from M-Bus device status) | [7 empty] | x |  |  |  |  | O
175 | Local disconnection M-Bus channel 2 | Indicates that the disconnector has been locally disconnected. | [7 empty] | x |  |  |  |  | M
176 | Local connection M-Bus channel 2 | Indicates that the disconnector has been locally connected. | [7 empty] | x |  |  |  |  | M
177 | reserved for future use
178 | reserved for future use
179 | reserved for future use
180 | Manual disconnection M-Bus channel 3 | Indicates that the disconnector has been manually disconnected. | [8 empty] | x |  |  |  | O
181 | Manual connection M-Bus channel 3 | Indicates that the disconnector has been manually connected. | [8 empty] | x |  |  |  | O
182 | Remote disconnection M-Bus channel 3 | Indicates that the disconnector has been remotely disconnected. | [8 empty] | x |  |  |  | M
183 | Remote connection M-Bus channel 3 | Indicates that the disconnector has been remotely connected. | [8 empty] | x |  |  |  | M
184 | Valve alarm M-Bus channel 3 | Indicates that a valve alarm has been registered. (Valve Alarm registered - flag from M-Bus device status) | [8 empty] | x |  |  |  | O
185 | Local disconnection M-Bus channel 3 | Indicates that the disconnector has been locally disconnected. | [8 empty] | x |  |  |  | M
186 | Local connection M-Bus channel 3 | Indicates that the disconnector has been locally connected. | [8 empty] | x |  |  |  | M
187 | reserved for future use
188 | reserved for future use
189 | reserved for future use
190 | Manual disconnection M-Bus channel 4 | Indicates that the disconnector has been manually disconnected. | [9 empty] | x |  |  | O
191 | Manual connection M-Bus channel 4 | Indicates that the disconnector has been manually connected. | [9 empty] | x |  |  | O
192 | Remote disconnection M-Bus channel 4 | Indicates that the disconnector has been remotely disconnected. | [9 empty] | x |  |  | M
193 | Remote connection M-Bus channel 4 | Indicates that the disconnector has been remotely connected. | [9 empty] | x |  |  | M
194 | Valve alarm M-Bus channel 4 | Indicates that a valve alarm has been registered. (Valve Alarm registered - flag from M-Bus device status) | [9 empty] | x |  |  | O
195 | Local disconnection M-Bus channel 4 | Indicates that the disconnector has been locally disconnected. | [9 empty] | x |  |  | M
196 | Local connection M-Bus channel 4 | Indicates that the disconnector has been locally connected. | [9 empty] | x |  |  | M
197 | reserved for future use
198 | reserved for future use
199 | reserved for future use
200 | Consumer interface de-activated | Indicates the de-activation of the consumer interface | x | [9 empty] | x |  | M
201 | Consumer interface re-activated | Indicates the re-activation of the consumer interface | x | [9 empty] | x |  | M
202 | manufacturer specific
203 | Modem Removed | It indicates that the modem has been removed from the meter. | x | [9 empty] | x |  | M-G
204 | G3 PSK change | Indicates the change of the G3-PLC PSK | x | [9 empty] | x |  | M-G3
205 | Load Relay change request - remote | Indicates that a remote request to change the load relay status was detected. | x | [11 empty] | M
206 | manufacturer specific
207 | manufacturer specific
208 | manufacturer specific
209 | manufacturer specific
210 | manufacturer specific
211 | manufacturer specific
212 | manufacturer specific
213 | manufacturer specific
214 | manufacturer specific
215 | manufacturer specific
216 | manufacturer specific
217 | manufacturer specific
218 | manufacturer specific
219 | manufacturer specific
220 | manufacturer specific
221 | manufacturer specific
222 | manufacturer specific
223 | manufacturer specific
224 | manufacturer specific
225 | manufacturer specific
226 | manufacturer specific
227 | manufacturer specific
228 | manufacturer specific
229 | manufacturer specific
230 | manufacturer specific
231 | manufacturer specific
232 | manufacturer specific
233 | manufacturer specific
234 | manufacturer specific
235 | manufacturer specific
236 | manufacturer specific
237 | manufacturer specific
238 | manufacturer specific
239 | manufacturer specific
240 | manufacturer specific
241 | manufacturer specific
242 | manufacturer specific
243 | manufacturer specific
244 | manufacturer specific
245 | manufacturer specific
246 | manufacturer specific
247 | manufacturer specific
248 | manufacturer specific
249 | manufacturer specific
250 | manufacturer specific
251 | manufacturer specific
252 | manufacturer specific
253 | manufacturer specific
254 | Load profile cleared | Any of the profiles cleared. NOTE: If it appears in Standard Event Log when any of the E-load profiles was cleared. | x | [11 empty] | M
255 | Event log cleared | Indicates that the event log was cleared. This is always the first entry in an event log. It is only stored in the affected event log. | x | x | x | x | x | x | x | x | x | x | x | x | M

## Communication Events
Event Code | Name | Description | Communication Event Log | Mandatory/optional/NA
1 | reserved for future use
2 | reserved for future use
3 | reserved for future use
4 | reserved for future use
5 | reserved for future use
6 | reserved for future use
7 | reserved for future use
8 | reserved for future use
9 | reserved for future use
10 | reserved for future use
11 | reserved for future use
12 | reserved for future use
13 | reserved for future use
14 | reserved for future use
15 | reserved for future use
16 | No connection timeout | There has been no remote communication on application layer for a predefined period of time; i.e. meter could not be reached remotely. | x | M-P2P
17 | Modem Initialization failure | Modem's response to initialization AT command(s) is invalid or ERROR or no response received | x | M-P2P
18 | SIM Card failure | SIM card is not inserted or is not recognized | x | M-P2P
19 | SIM Card ok | SIM card has been correctly detected | x | M-P2P
20 | GSM registration failure | Modem's registration on GSM network was not successful | x | M-P2P
21 | GPRS registration failure | Modem's registration on GPRS network was not successful | x | M-P2P
22 | PDP context established | PDP context is established | x | M-P2P
23 | PDP context destroyed | PDP context is destroyed | x | M-P2P
24 | PDP context failure | No Valid PDP context(s) retrieved | x | M-P2P
25 | Modem SW reset | Modem restarted by SW reset | x | O-P2P
26 | Modem HW reset | Modem restarted by HW reset (this event is not issued after a general power resume) | x | M-P2P
27 | GSM outgoing connection | Modem is successfully connected, initiated by an outgoing call. | x | O-P2P
28 | GSM incoming connection | Modem is successfully connected, initiated by an incoming call | x | O-P2P
29 | GSM hang-up | Modem is disconnected | x | O-P2P
30 | Diagnostic failure | Modem's response to diagnostic AT command(s) ("+CPIN?", "+CSQ", "+CREG?", "+CGREG?", "+COPS?", "+CGACT?", "+CPMS?") is invalid or ERROR or no response received. | x | M-P2P
31 | User initialization failure | Modem's initialization AT command(s ) – specified in attribute 3 of the modem configuration object - is invalid. Error message or no response from the modem. | x | M-P2P
32 | Signal quality low | Signal strength too low, not known, or not detectable | x | M-P2P
33 | Auto Answer Number of calls exceeded | Number of calls has exceeded (in mode(1) or mode(2) ) the values given in the attribute number_of_calls. | x | O-P2P
34 | ping_response_not_received | the modem fails to receive the response | x | M-P2P
35 | TCP/IP_connection_establishment_failure | the modem fails to establish the TCP connection with the head end system | x | M-P2P
36 | Ack_not_received | modem fails to receive the acknowledgement of a frame which has been sent | x | M-P2P
37 | Signal quality low end | Signal strength becomes normally after event 32 occurs. | x | M-P2P
38 | ping_response_not_received | Ping response start to receive after after event 34 occurs. | x | M-P2P
39 | reserved for future use
40 | reserved for future use
41 | reserved for future use
42 | reserved for future use
43 | reserved for future use
44 | reserved for future use
45 | reserved for future use
46 | reserved for future use
47 | reserved for future use
48 | reserved for future use
49 | reserved for future use
50 | reserved for future use
51 | reserved for future use
52 | reserved for future use
53 | reserved for future use
54 | reserved for future use
55 | reserved for future use
56 | reserved for future use
57 | reserved for future use
58 | reserved for future use
59 | reserved for future use
60 | reserved for future use
61 | reserved for future use
62 | reserved for future use
63 | reserved for future use
64 | reserved for future use
65 | reserved for future use
66 | reserved for future use
67 | reserved for future use
68 | reserved for future use
69 | reserved for future use
70 | reserved for future use
71 | reserved for future use
72 | reserved for future use
73 | reserved for future use
74 | reserved for future use
75 | reserved for future use
76 | reserved for future use
77 | reserved for future use
78 | reserved for future use
79 | reserved for future use
80 | reserved for future use
81 | reserved for future use
82 | reserved for future use
83 | reserved for future use
84 | reserved for future use
85 | reserved for future use
86 | reserved for future use
87 | reserved for future use
88 | reserved for future use
89 | reserved for future use
90 | reserved for future use
91 | reserved for future use
92 | reserved for future use
93 | reserved for future use
94 | reserved for future use
95 | reserved for future use
96 | reserved for future use
97 | reserved for future use
98 | reserved for future use
99 | reserved for future use
100 | reserved for future use
101 | reserved for future use
102 | reserved for future use
103 | reserved for future use
104 | reserved for future use
105 | reserved for future use
106 | reserved for future use
107 | reserved for future use
108 | reserved for future use
109 | reserved for future use
110 | reserved for future use
111 | reserved for future use
112 | reserved for future use
113 | reserved for future use
114 | reserved for future use
115 | reserved for future use
116 | reserved for future use
117 | reserved for future use
118 | reserved for future use
119 | reserved for future use
120 | reserved for future use
121 | reserved for future use
122 | reserved for future use
123 | reserved for future use
124 | reserved for future use
125 | reserved for future use
126 | reserved for future use
127 | reserved for future use
128 | No connection timeout | Meter that has not been individually addressed for the PLCG3 Timeout, it returns to the non associated state and loses its PAN coordinator |  | M-G3
129 | Modem Initialization failure | G3-PLC Modem's response to initialization is invalid or ERROR or no response received |  | M-G3
130 | PAN registration success | Indicates successfull registration to a PAN coordinator |  | M-G3
131 | PAN disconnect - KICK | Indicates that the Meter was kicked off the network (received kick-off command)by the PAN coordinator |  | M-G3
132 | PAN registration failure | Indicates failed registration to a PAN coordinator after maximum retries |  | M-G3
133 | ICMP RA received | Indicates the ceceiption of an ICMP Router Advertisement from the PAN coordinator |  | M-G3
134 | ICMP RS failure | Indicates that the maximum number of ICMP Router Solicitation have been sent to the PAN coordinator without receiption of an ICMP RA |  | M-G3
135 | ICMP echo request received | Indicates the receiption of an ICMP echo request from the PAN coordinator (and sending a reply) |  | M-G3
136 | Modem SW reset | Modem restarted by SW reset |  | O-G3
137 | Modem HW reset | Modem restarted by HW reset (this event is not issued after a general power resume) |  | M-G3
138 | reserved for future use
139 | reserved for future use
140 | reserved for future use
141 | reserved for future use
142 | reserved for future use
143 | reserved for future use
144 | reserved for future use
145 | reserved for future use
146 | reserved for future use
147 | reserved for future use
148 | reserved for future use
149 | reserved for future use
150 | reserved for future use
151 | reserved for future use
152 | reserved for future use
153 | reserved for future use
154 | reserved for future use
155 | reserved for future use
156 | reserved for future use
157 | reserved for future use
158 | reserved for future use
159 | reserved for future use
160 | reserved for future use
161 | reserved for future use
162 | reserved for future use
163 | reserved for future use
164 | reserved for future use
165 | reserved for future use
166 | reserved for future use
167 | reserved for future use
168 | reserved for future use
169 | reserved for future use
170 | reserved for future use
171 | reserved for future use
172 | reserved for future use
173 | reserved for future use
174 | reserved for future use
175 | reserved for future use
176 | reserved for future use
177 | reserved for future use
178 | reserved for future use
179 | reserved for future use
180 | reserved for future use
181 | reserved for future use
182 | reserved for future use
183 | reserved for future use
184 | reserved for future use
185 | reserved for future use
186 | reserved for future use
187 | reserved for future use
188 | reserved for future use
189 | reserved for future use
190 | reserved for future use
191 | reserved for future use
192 | reserved for future use
193 | reserved for future use
194 | reserved for future use
195 | reserved for future use
196 | reserved for future use
197 | reserved for future use
198 | reserved for future use
199 | reserved for future use
200 | reserved for future use
201 | reserved for future use
202 | reserved for future use
203 | reserved for future use
204 | reserved for future use
205 | reserved for future use
206 | reserved for future use
207 | reserved for future use
208 | reserved for future use
209 | reserved for future use
210 | reserved for future use
211 | reserved for future use
212 | reserved for future use
213 | reserved for future use
214 | reserved for future use
215 | reserved for future use
216 | reserved for future use
217 | reserved for future use
218 | reserved for future use
219 | reserved for future use
220 | reserved for future use
221 | reserved for future use
222 | reserved for future use
223 | reserved for future use
224 | reserved for future use
225 | reserved for future use
226 | reserved for future use
227 | reserved for future use
228 | reserved for future use
229 | reserved for future use
230 | reserved for future use
231 | reserved for future use
232 | reserved for future use
233 | reserved for future use
234 | reserved for future use
235 | reserved for future use
236 | reserved for future use
237 | reserved for future use
238 | reserved for future use
239 | reserved for future use
240 | reserved for future use
241 | reserved for future use
242 | reserved for future use
243 | reserved for future use
244 | reserved for future use
245 | reserved for future use
246 | reserved for future use
247 | reserved for future use
248 | reserved for future use
249 | reserved for future use
250 | reserved for future use
251 | reserved for future use
252 | reserved for future use
253 | reserved for future use
254 | reserved for future use
255 | Event log cleared | Indicates that the event log was cleared. This is always the first entry in an event log. It is only stored in the affected event log. | x | M

## Error and Alarms
Assignment of Error Register/Alarm Register 1 bits |  |  | Assignment of Alarm Register 2 bits |  |  | Assignment of Alarm Register 3 bits
Bit | Alarm | Triggering event | Bit | Alarm | Triggering event | Bit | Alarm | Triggering event
0 | Clock invalid | 6 | 0 | Total Power Failure | 1 | 0 | Disconnector ready for manual reconnection | 59
1 | Battery replace | 7 | 1 | Power Resume | 2 | 1 | Manual disconnection | 60
2 | Reserved for future use | - | 2 | Voltage Missing Phase L1 | 82 | 2 | Manual connection | 61
3 | Reserved for future use | - | 3 | Voltage Missing Phase L2 | 83 | 3 | Remote disconnection | 62
4 | Reserved for future use | - | 4 | Voltage Missing Phase L3 | 84 | 4 | Remote connection | 63
5 | Reserved for future use | - | 5 | Voltage Normal Phase L1 | 85 | 5 | Local disconnection | 64
6 | Reserved for future use | - | 6 | Voltage Normal Phase L2 | 86 | 6 | Local reconnection | 69
7 | Reserved for future use | - | 7 | Voltage Normal Phase L3 | 87 | 7 | Load Relay change request - remote | 205
8 | Program memory error | 12 | 8 | Missing Neutral | 89 | 8 | Limiter threshold exceeded | 65
9 | RAM error | 13 | 9 | Phase Asymmetry | 90 | 9 | Limiter threshold config changed | 67
10 | NV memory error | 14 | 10 | Current Reversal | 91 | 10 | Firmware ready for activation | 17
11 | Measurement system error | 16 | 11 | Wrong Phase Sequence | 88 | 11 | Firmware activated | 18
12 | Watchdog error | 15 | 12 | Unexpected Consumption | 52 | 12 | FW verification/activation failed | 51
13 | Fraud attempt | 40, 42, 44, 46, 49, 50, 54 | 13 | Key Exchanged | 48 | 13 | FOTA upgrading sucessfully | 31
14 | Reserved for future use | - | 14 | Bad Voltage Quality L1 | 92 | 14 | FOTA upgrading failed | 32
15 | Reserved for future use | - | 15 | Bad Voltage Quality L2 | 93 | 15 | One or more parameters changed | 47
16 | M-Bus communication error ch1 | 100 | 16 | Bad Voltage Quality L3 | 94 | 16 | Capturing of load profile 1 enabled | 22
17 | M-Bus communication error ch2 | 110 | 17 | External Alert | 20 | 17 | Capturing of load profile 1 disabled | 23
18 | M-Bus communication error ch3 | 120 | 18 | Local communication attempt | 53 | 18 | Capturing of load profile 2 enabled | 24
19 | M-Bus communication error ch4 | 130 | 19 | New M-Bus Device Installed Ch1 | 105 | 19 | Capturing of load profile 2 disabled | 25
20 | M-Bus fraud attempt ch1 | 103 | 20 | New M-Bus Device Installed Ch2 | 115 | 20
21 | M-Bus fraud attempt ch2 | 113 | 21 | New M-Bus Device Installed Ch3 | 125 | 21
22 | M-Bus fraud attempt ch3 | 123 | 22 | New M-Bus Device Installed Ch4 | 135 | 22
23 | M-Bus fraud attempt ch4 | 133 | 23 | Reserved for future use | - | 23
24 | Permanent error M-bus ch1 | 106 | 24 | Reserved for future use | - | 24
25 | Permanent error M-bus ch2 | 116 | 25 | Reserved for future use | - | 25
26 | Permanent error M-bus ch3 | 126 | 26 | Reserved for future use | - | 26
27 | Permanent error M-bus ch4 | 136 | 27 | M-Bus valve alarm Ch1 | 164 | 27
28 | Battery low on M-bus ch1 | 102 | 28 | M-Bus valve alarm Ch2 | 174 | 28
29 | Battery low on M-bus ch2 | 112 | 29 | M-Bus valve alarm Ch3 | 184 | 29
30 | Battery low on M-bus ch3 | 122 | 30 | M-Bus valve alarm Ch4 | 194 | 30
31 | Battery low on M-bus ch4 | 132 | 31 | Disconnect/Reconnect Failure | 68 | 31

## P2P Error codes
Assignment of P2P Communication Error code
Code | Cause
PS internal cause
1 | Invalid connection identifier
2 | Invalid NSAPI
3 | Invalid Primary NSAPI
4 | Invalid field
5 | SNDCP failure
6 | RAB setup failure
7 | No GPRS context
8 | PDP establish timeout
9 | PDP activate timeout
10 | PDP modify timeout
11 | PDP inactive max timeout
12 | PDP lowerlayer error
13 | PDP duplicate
14 | Access technology change
15 | PDP unknown reason
PS network cause
16 | LLC or SNDCP failure
17 | Insufficient resources
18 | Missing or unknown APN
19 | Unknown PDP address or PDP type
20 | User Aauthentication failed
21 | Activation rejected by GGSN
22 | Activation rejected, unspecified
23 | Service option not supported
24 | Requested service option not subscribed
25 | Service option temporarily out of order
26 | NSAPI already used (not sent)
27 | Regular deactivation
28 | QoS not accepted
29 | Network failure
30 | Reactivation required
31 | Feature not supported
32 | Semantic error in the TFT operation
33 | Syntactical error in the TFT operation
34 | Unknown PDP context
35 | PDP context without TFT already activated
36 | Semantic errors in packet filter
37 | Syntactical errors in packet filter
38 | Invalid transaction identifier
39 | Semantically incorrect message
40 | Invalid mandatory information
41 | Message non-existent/not implemented
42 | Message type not compatible with state
43 | IE non-existent/not implemented
44 | Conditional IE error
45 | Message not compatible with state
46 | Protocol error, unspecified

## Display Configuration
Display Configuration Data Elements
Capture object definition | Description of the value displayed | OBIS Code (Display) | Value (Display) DC | Value (Display) CT | Unit (Display)
{1,0-0:0.9.1.255,2,0} | Local Time | 0.9.1 | 12:53 | 12:53
{1,0-0:0.9.2.255,2,0} | Local Date | 0.9.2 | 15.02.2017 | 15.02.2017
{1,0-0:97.97.128.255,2,0} | Fatal Error Register | F.F | A1B2C3D4 | A1B2C3D4
{1,0-0:97.97.0.255,2,0} | Error Register | 97.97.0 | A1B2C3D4 | A1B2C3D4
{1,0-0:96.1.0.255,2,0} | Device ID 1, manufacturing number | 96.1.0 | A1B2C3D4 | A1B2C3D4
{1,1-0:0.2.1.255,2,0} | Parameter Record Number | 0.2.1 | A1B2C3D4 | A1B2C3D4
{1,0-0:0.1.0.255,2,0} | Billing Period Counter (VZ) | 0.1.0 | 12 | 12
{1,0-0:0.1.2.101,2,0}, | Billing Timestamp - last billing timestamp | 0.1.2.(VZ) | 12:34 01.02.17 | 12:34 01.02.17
{1,0-0:0.1.2.102,2,0}, | Billing Timestamp - 2nd to last billing timestamp | 0.1.2.(VZ-1) | 12:34 01.01.17 | 12:34 01.01.17
{3,1-0:1.8.0.255,2,0}, | Active energy import (+A) - current value | 1.8.0 | 123456.78 | 12345,678 | kWh
{3,1-0:1.8.0.101,2,0}, | Active energy import (+A) - last billing value | 1.8.0.(VZ) | 123456.78 | 12345,679 | kWh
{3,1-0:1.8.0.102,2,0}, | Active energy import (+A) - 2nd to last billing value | 1.8.0.(VZ-1) | 123456.78 | 12345,680 | kWh
{3,1-0:1.8.1.255,2,0}, | Active energy import (+A) rate 1 - current value | 1.8.1 | 123456.78 | 12345,681 | kWh
{3,1-0:1.8.1.101,2,0}, | Active energy import (+A) rate 1 - last billing value | 1.8.1.(VZ) | 123456.78 | 12345,682 | kWh
{3,1-0:1.8.1.102,2,0}, | Active energy import (+A) rate 1 - 2nd to last billing value | 1.8.1.(VZ-1) | 123456.78 | 12345,683 | kWh
{3,1-0:1.8.2.255,2,0}, | Active energy import (+A) rate 2 - current value | 1.8.2 | 123456.78 | 12345,684 | kWh
{3,1-0:1.8.2.101,2,0}, | Active energy import (+A) rate 2 - last billing value | 1.8.2.(VZ) | 123456.78 | 12345,685 | kWh
{3,1-0:1.8.2.102,2,0}, | Active energy import (+A) rate 2 - 2nd to last billing value | 1.8.2.(VZ-1) | 123456.78 | 12345,686 | kWh
{3,1-0:2.8.0.255,2,0}, | Active energy export (-A) - current value | 2.8.0 | 123456.78 | 12345,687 | kWh
{3,1-0:2.8.0.101,2,0}, | Active energy export (-A) - last billing value | 2.8.0.(VZ) | 123456.78 | 12345,688 | kWh
{3,1-0:2.8.0.102,2,0}, | Active energy export (-A) - 2nd to last billing value | 2.8.0.(VZ-1) | 123456.78 | 12345,689 | kWh
{3,1-0:2.8.1.255,2,0}, | Active energy export (-A) rate 1 - current value | 2.8.1 | 123456.78 | 12345,690 | kWh
{3,1-0:2.8.1.101,2,0}, | Active energy export (-A) rate 1 - last billing value | 2.8.1.(VZ) | 123456.78 | 12345,691 | kWh
{3,1-0:2.8.1.102,2,0}, | Active energy export (-A) rate 1 - 2nd to last billing value | 2.8.1.(VZ-1) | 123456.78 | 12345,692 | kWh
{3,1-0:2.8.2.255,2,0}, | Active energy export (-A) rate 2 - current value | 2.8.2 | 123456.78 | 12345,693 | kWh
{3,1-0:2.8.2.101,2,0}, | Active energy export (-A) rate 2 - last billing value | 2.8.2.(VZ) | 123456.78 | 12345,694 | kWh
{3,1-0:2.8.2.102,2,0}, | Active energy export (-A) rate 2 - 2nd to last billing value | 2.8.2.(VZ-1) | 123456.78 | 12345,695 | kWh
{3,1-0:3.8.0.255,2,0}, | Reactive energy import (+R) - current value | 3.8.0 | 123456.78 | 12345,696 | kvarh
{3,1-0:3.8.0.101,2,0}, | Reactive energy import (+R) - last billing value | 3.8.0.(VZ) | 123456.78 | 12345,697 | kvarh
{3,1-0:3.8.0.102,2,0}, | Reactive energy import (+R) - 2nd to last billing value | 3.8.0.(VZ-1) | 123456.78 | 12345,698 | kvarh
{3,1-0:3.8.1.255,2,0}, | Reactive energy import (+R) rate 1 - current value | 3.8.1 | 123456.78 | 12345,699 | kvarh
{3,1-0:3.8.1.101,2,0}, | Reactive energy import (+R) rate 1 - last billing value | 3.8.1.(VZ) | 123456.78 | 12345,700 | kvarh
{3,1-0:3.8.1.102,2,0}, | Reactive energy import (+R) rate 1 - 2nd to last billing value | 3.8.1.(VZ-1) | 123456.78 | 12345,701 | kvarh
{3,1-0:3.8.2.255,2,0}, | Reactive energy import (+R) rate 2 - current value | 3.8.2 | 123456.78 | 12345,702 | kvarh
{3,1-0:3.8.2.101,2,0}, | Reactive energy import (+R) rate 2 - last billing value | 3.8.2.(VZ) | 123456.78 | 12345,703 | kvarh
{3,1-0:3.8.2.102,2,0}, | Reactive energy import (+R) rate 2 - 2nd to last billing value | 3.8.2.(VZ-1) | 123456.78 | 12345,704 | kvarh
{3,1-0:4.8.0.255,2,0}, | Reactive energy export (-R) - current value | 4.8.0 | 123456.78 | 12345,705 | kvarh
{3,1-0:4.8.0.101,2,0}, | Reactive energy export (-R) - last billing value | 4.8.0.(VZ) | 123456.78 | 12345,706 | kvarh
{3,1-0:4.8.0.102,2,0}, | Reactive energy export (-R) - 2nd to last billing value | 4.8.0.(VZ-1) | 123456.78 | 12345,707 | kvarh
{3,1-0:4.8.1.255,2,0}, | Reactive energy export (-R) rate 1 - current value | 4.8.1 | 123456.78 | 12345,708 | kvarh
{3,1-0:4.8.1.101,2,0}, | Reactive energy export (-R) rate 1 - last billing value | 4.8.1.(VZ) | 123456.78 | 12345,709 | kvarh
{3,1-0:4.8.1.102,2,0}, | Reactive energy export (-R) rate 1 - 2nd to last billing value | 4.8.1.(VZ-1) | 123456.78 | 12345,710 | kvarh
{3,1-0:4.8.2.255,2,0}, | Reactive energy export (-R) rate 2 - current value | 4.8.2 | 123456.78 | 12345,711 | kvarh
{3,1-0:4.8.2.101,2,0}, | Reactive energy export (-R) rate 2 - last billing value | 4.8.2.(VZ) | 123456.78 | 12345,712 | kvarh
{3,1-0:4.8.2.102,2,0}, | Reactive energy export (-R) rate 2 - 2nd to last billing value | 4.8.2.(VZ-1) | 123456.78 | 12345,713 | kvarh
{5,1-0:1.4.0.255,2,0}, | Demand Active energy import (+A) - current value | 1.4.0 | xxx 12,34 | xxx 1,234 | kW
{5,1-0:2.4.0.255,2,0}, | Demand Active energy export (-A) - current value | 2.4.0 | xxx 12,34 | xxx 1,235 | kW
{5,1-0:3.4.0.255,2,0}, | Demand Rective energy import (+R) - current value | 3.4.0 | xxx 12,34 | xxx 1,236 | kvar
{5,1-0:4.4.0.255,2,0}, | Demand Reactive energy export (-R) - current value | 4.4.0 | xxx 12,34 | xxx 1,237 | kvar
{4,1-0:1.6.0.255,2,0}, | Max Demand Active energy import (+A) - current value | 1.6.0 | 12.34 | 1,234 | kW
{4,1-0:1.6.0.255,5,0}, | Max Demand Active energy import (+A) - current timestamp | 1.6.0 | 12:34 01.02.17 | 12:34 01.02.17
{4,1-0:1.6.0.101,2,0}, | Max Demand Active energy import (+A) - last billing value | 1.6.0.(VZ) | 12.34 | 1,234 | kW
{4,1-0:1.6.0.101,5,0}, | Max Demand Active energy import (+A) - last billing timestamp | 1.6.0.(VZ) | 12:34 01.01.17 | 12:34 01.01.17
{4,1-0:1.6.0.102,2,0}, | Max Demand Active energy import (+A) - 2nd to last billing value | 1.6.0.(VZ-1) | 12.34 | 1,234 | kW
{4,1-0:1.6.0.102,5,0}, | Max Demand Active energy import (+A) - 2nd to last billing timestamp | 1.6.0.(VZ-1) | 12:34 14.02.17 | 12:34 14.02.17
{4,1-0:2.6.0.255,2,0}, | Max Demand Active energy export (-A) - current value | 2.6.0 | 12.34 | 1,234 | kW
{4,1-0:2.6.0.255,5,0}, | Max Demand Active energy export (-A) - current timestamp | 2.6.0 | 12:34 01.02.17 | 12:34 01.02.17
{4,1-0:2.6.0.101,2,0}, | Max Demand Active energy export (-A) - last billing value | 2.6.0.(VZ) | 12.34 | 1,234 | kW
{4,1-0:2.6.0.101,5,0}, | Max Demand Active energy export (-A) - last billing timestamp | 2.6.0.(VZ) | 12:34 01.01.17 | 12:34 01.01.17
{4,1-0:2.6.0.102,2,0}, | Max Demand Active energy export (-A) - 2nd to last billing value | 2.6.0.(VZ-1) | 12.34 | 1,234 | kW
{4,1-0:2.6.0.102,5,0}, | Max Demand Active energy export (-A) - 2nd to last billing timestamp | 2.6.0.(VZ-1) | 12:34 01.02.17 | 12:34 01.02.17
{4,1-0:3.6.0.255,2,0}, | Max Demand Reactive energy import (+R) - current value | 3.6.0 | 12.34 | 1,234 | kvar
{4,1-0:3.6.0.255,5,0}, | Max Demand Reactive energy import (+R) - current timestamp | 3.6.0 | 12:34 01.02.17 | 12:34 01.02.17
{4,1-0:3.6.0.101,2,0}, | Max Demand Reactive energy import (+R) - last billing value | 3.6.0.(VZ) | 12.34 | 1,234 | kvar
{4,1-0:3.6.0.101,5,0}, | Max Demand Reactive energy import (+R) - last billing timestamp | 3.6.0.(VZ) | 12:34 01.01.17 | 12:34 01.01.17
{4,1-0:3.6.0.102,2,0}, | Max Demand Reactive energy import (+R) - 2nd to last billing value | 3.6.0.(VZ-1) | 12.34 | 1,234 | kvar
{4,1-0:3.6.0.102,5,0}, | Max Demand Reactive energy import (+R) - 2nd to last billing timestamp | 3.6.0.(VZ-1) | 12:34 14.02.17 | 12:34 14.02.17
{4,1-0:4.6.0.255,2,0}, | Max Demand Reactive energy export (-R) - current value | 4.6.0 | 12.34 | 1,234 | kvar
{4,1-0:4.6.0.255,5,0}, | Max Demand Reactive energy export (-R) - current timestamp | 4.6.0 | 12:34 01.02.17 | 12:34 01.02.17
{4,1-0:4.6.0.101,2,0}, | Max Demand Reactive energy export (-R) - last billing value | 4.6.0.(VZ) | 12.34 | 1,234 | kvar
{4,1-0:4.6.0.101,5,0}, | Max Demand Reactive energy export (-R) - last billing timestamp | 4.6.0.(VZ) | 12:34 01.01.17 | 12:34 01.01.17
{4,1-0:4.6.0.102,2,0}, | Max Demand Reactive energy export (-R) - 2nd to last billing value | 4.6.0.(VZ-1) | 12.34 | 1,234 | kvar
{4,1-0:4.6.0.102,5,0}, | Max Demand Reactive energy export (-R) - 2nd to last billing timestamp | 4.6.0.(VZ-1) | 12:34 01.02.17 | 12:34 01.02.17
{3,1-0:1.2.0.255,2,0}, | Cumulative Max Demand Active energy import (+A) - current value | 1.2.0 | 1234,56 | 123,456 | kW
{3,1-0:2.2.0.255,2,0}, | Cumulative Max Demand Active energy export (-A) - current value | 2.2.0 | 1234,56 | 123,456 | kW
{3,1-0:3.2.0.255,2,0}, | Cumulative Max Demand Reactive energy import (+R) - current value | 3.2.0 | 1234,56 | 123,456 | kvar
{3,1-0:4.2.0.255,2,0}, | Cumulative Max Demand Reactive energy export (-R) - current value | 4.2.0 | 1234,56 | 123,456 | kvar
{1,1-0:0.2.0.255,2,0}, | Active firmware version (LR) | 0.2.0 | A1B2C3D4 | A1B2C3D4
{1,1-0:0.2.8.255,2,0}, | Active firmware signature (LR) | 0.2.8 | A1B2C3D4 | A1B2C3D4
{1,1-1:0.2.0.255,2,0}, | Active firmware version (LNR) | 1.1.0.2.0 | A1B2C3D4 | A1B2C3D4
{1,1-1:0.2.8.255,2,0}, | Active firmware signature (LNR) | 1.1.0.2.8 | A1B2C3D4 | A1B2C3D4
{1,1-2:0.2.0.255,2,0}, | Active firmware version (Comms) | 1.2.0.2.0 | A1B2C3D4 | A1B2C3D4
{1,1-2:0.2.8.255,2,0}, | Active firmware signature (comms) | 1.2.0.2.8 | A1B2C3D4 | A1B2C3D4
{3,1-0:1.7.0.255,2,0}, | Instantaneous active import power (+P) | 1.7.0 | 12.34 | 1,234 | kW
{3,1-0:2.7.0.255,2,0}, | Instantaneous active export power (-P) | 2.7.0 | 12.34 | 1,234 | kW
{3,1-0:3.7.0.255,2,0}, | Instantaneous reactive import power (+Q) | 3.7.0 | 12.34 | 1,234 | kvar
{3,1-0:4.7.0.255,2,0}, | Instantaneous reactive export power (-Q) | 4.7.0 | 12.34 | 1,234 | kvar
{3,1-0:9.7.0.255,2,0}, | Instantaneous apparent import power (+S) | 9.7.0 | 12.34 | 1,234 | kVA
{3,1-0:10.7.0.255,2,0}, | Instantaneous apparent export power (-S) | 10.7.0 | 12.34 | 1,234 | kVA
{3,1-0:90.7.0.255,2,0}, | Instantaneous current (sum over all phases) | 90.7.0 | 123,4 | 12,34 | A
{3,1-0:13.7.0.255,2,0}, | Instantaneous Power factor import (¦+P/+S¦) | 13.7.0 | 1,234 | 1,234
{3,1-0:84.7.0.255,2,0}, | Instantaneous Power factor export (¦-P/-S¦) | 84.7.0 | 1,234 | 1,234
{3,1-0:14.7.0.255,2,0}, | Instantaneous net frequency; any phase | 14.7.0 | 12.34 | 12.34 | Hz
{3,1-0:21.7.0.255,2,0}, | Instantaneous active import power (+P) L1 | 21.7.0 | 12.34 | 1,234 | kW
{3,1-0:22.7.0.255,2,0}, | Instantaneous active export power (-P) L1 | 22.7.0 | 12.34 | 1,234 | kW
{3,1-0:23.7.0.255,2,0}, | Instantaneous reactive import power (+Q) L1 | 23.7.0 | 12.34 | 1,234 | kvar
{3,1-0:24.7.0.255,2,0}, | Instantaneous reactive export power (-Q) L1 | 24.7.0 | 12.34 | 1,234 | kvar
{3,1-0:29.7.0.255,2,0}, | Instantaneous apparent import power (+S) L1 | 29.7.0 | 12.34 | 1,234 | kVA
{3,1-0:30.7.0.255,2,0}, | Instantaneous apparent export power (-S) L1 | 30.7.0 | 12.34 | 1,234 | kVA
{3,1-0:31.7.0.255,2,0}, | Instantaneous current L1 | 31.7.0 | 123,4 | 12,34 | A
{3,1-0:32.7.0.255,2,0}, | Instantaneous voltage L1 | 32.7.0 | 123,4 | 123,4 | V
{3,1-0:33.7.0.255,2,0}, | Instantaneous Power factor import (¦+P/+S¦) L1 | 33.7.0 | 1,234 | 1,234
{3,1-0:85.7.0.255,2,0}, | Instantaneous Power factor export (¦-P/-S¦) L1 | 85.7.0 | 1,234 | 1,234
{3,1-0:41.7.0.255,2,0}, | Instantaneous active import power (+P) L2 | 41.7.0 | 12.34 | 1,234 | kW
{3,1-0:42.7.0.255,2,0}, | Instantaneous active export power (-P) L2 | 42.7.0 | 12.34 | 1,234 | kW
{3,1-0:43.7.0.255,2,0}, | Instantaneous reactive import power (+Q) L2 | 43.7.0 | 12.34 | 1,234 | kvar
{3,1-0:44.7.0.255,2,0}, | Instantaneous reactive export power (-Q) L2 | 44.7.0 | 12.34 | 1,234 | kvar
{3,1-0:49.7.0.255,2,0}, | Instantaneous apparent import power (+S) L2 | 49.7.0 | 12.34 | 1,234 | kVA
{3,1-0:50.7.0.255,2,0}, | Instantaneous apparent export power (-S) L2 | 50.7.0 | 12.34 | 1,234 | kVA
{3,1-0:51.7.0.255,2,0}, | Instantaneous current L2 | 51.7.0 | 123,4 | 12,34 | A
{3,1-0:52.7.0.255,2,0}, | Instantaneous voltage L2 | 52.7.0 | 123,4 | 123,4 | V
{3,1-0:53.7.0.255,2,0}, | Instantaneous Power factor import (¦+P/+S¦) L2 | 53.7.0 | 1,234 | 1,234
{3,1-0:86.7.0.255,2,0}, | Instantaneous Power factor export (¦-P/-S¦) L2 | 86.7.0 | 1,234 | 1,234
{3,1-0:61.7.0.255,2,0}, | Instantaneous active import power (+P) L3 | 61.7.0 | 12.34 | 1,234 | kW
{3,1-0:62.7.0.255,2,0}, | Instantaneous active export power (-P) L3 | 62.7.0 | 12.34 | 1,234 | kW
{3,1-0:63.7.0.255,2,0}, | Instantaneous reactive import power (+Q) L3 | 63.7.0 | 12.34 | 1,234 | kvar
{3,1-0:64.7.0.255,2,0}, | Instantaneous reactive export power (-Q) L3 | 64.7.0 | 12.34 | 1,234 | kvar
{3,1-0:69.7.0.255,2,0}, | Instantaneous apparent import power (+S) L3 | 69.7.0 | 12.34 | 1,234 | kVA
{3,1-0:70.7.0.255,2,0}, | Instantaneous apparent export power (-S) L3 | 70.7.0 | 12.34 | 1,234 | kVA
{3,1-0:71.7.0.255,2,0}, | Instantaneous current L3 | 71.7.0 | 123,4 | 12,34 | A
{3,1-0:72.7.0.255,2,0}, | Instantaneous voltage L3 | 72.7.0 | 123,4 | 123,4 | V
{3,1-0:73.7.0.255,2,0}, | Instantaneous Power factor import (¦+P/+S¦) L3 | 73.7.0 | 1,234 | 1,234
{3,1-0:87.7.0.255,2,0}, | Instantaneous Power factor export (¦-P/-S¦) L3 | 87.7.0 | 1,234 | 1,234
{3,1-0:81.7.40.255,2,0}, | Instantaneous Phase Angle (U(L1) to I(L1)) | 81.7.40 | 123 | 123 | °
{3,1-0:81.7.51.255,2,0}, | Instantaneous Phase Angle (U(L2) to I(L2)) | 81.7.51 | 123 | 123 | °
{3,1-0:81.7.62.255,2,0}, | Instantaneous Phase Angle (U(L3) to I(L3)) | 81.7.62 | 123 | 123 | °

## pre-defined data types
Predefined data types
type_name=type_string
The identifier before the '=' is replaced by the string after the '='
No spaces are allowed before and after the '='
asslist_type=array(struct(long_unsigned, octet_string))
object_list_type=array(object_list_element)
object_list_element=struct(long_unsigned, unsigned, octet_string, access_right)
access_right=struct(attribute_access_descriptor, method_access_descriptor)
attribute_access_descriptor=array(attribute_access_item)
method_access_descriptor=array(method_access_item)
attribute_access_item=struct(integer, enum, access_selector)
access_selector=choice(array(integer),null)
method_access_item=struct(integer, enum)
associated_partners_type=struct(integer,long_unsigned)
application_context_name=choice(struct(unsigned, unsigned, long_unsigned, unsigned, unsigned, unsigned, unsigned), octet_string)
xDLMS_context_type=struct(bit_string, long_unsigned, long_unsigned, unsigned, integer, octet_string)
mechanism_name_structure=application_context_name
scal_unit_type=struct(integer, enum)
scripts=array(script9)
script9=struct(long_unsigned, array(action_specification))
action_specification=struct(enum, long_unsigned, octet_string[6], integer, any)
script22=struct(octet_string[6], long_unsigned)
value_definition=struct(long_unsigned, octet_string, integer)
threshold=any
emergency_profile_type=struct(long_unsigned, octet_string, double_long_unsigned)
action_set=struct(action_item, action_item)
action_item=struct(octet_string, long_unsigned)
frequencies_type=struct(double_long_unsigned, double_long_unsigned)
initiator_descriptor=struct(octet_string, long_unsigned, unsigned)
desynchronization_listing_type=struct(double_long_unsigned, double_long_unsigned, double_long_unsigned, double_long_unsigned, double_long_unsigned)
capture_object_definition=struct(long_unsigned, octet_string, integer, long_unsigned)
send_destination_and_method_type=struct(enum, octet_string, enum)
window_element=struct(octet_string, octet_string)
caller_id=(octet_string)
list_of_allowed_callers_element=struct(octet_string, enum)
sender_id=(octet_string)
senders_and_actions_element=struct(octet_string, script22)
callback_data=struct(boolean, unsigned, octet_string)
LCP_options_element=struct(unsigned, unsigned, choice(unsigned, boolean, long_unsigned, double_long_unsigned, callback_data))
IPCP_options_element=struct(unsigned, unsigned, choice(boolean, long_unsigned, double_long_unsigned, array(double_long_unsigned)))
PPP_authentication_type=choice(NULL, struct(octet_string, octet_string), struct(octet_string, unsigned), struct(boolean, boolean, boolean))
quality_of_service_type=struct(qos_element, qos_element)
qos_element=struct(unsigned, unsigned, unsigned, unsigned, unsigned)
nr_rings_type=struct(unsigned, unsigned)
cell_info_type=struct(double_long_unsigned,long_ unsigned,unsigned,unsigned,long_ unsigned,long_ unsigned,double_long_ unsigned)
IPv6_address=octet_string[0..48]
IPv6_address_entry=(enum, IPv6_address)
register_assignment_item=struct(long_unsigned,octet_string[6])
execution_time_date=struct(octet_string,octet_string)
reply_status=struct(unsigned,unsigned)
neighbour_discovery_setup_element=struct(unsigned,long_unsigned,double_long_unsigned)
certificate_info=struct(enum,enum,octet_string,octet_string,octet_string)
key_transfer=array(struct(enum,octet_string))
key_agreement=array(struct(enum,octet_string))
user_list_entry=struct(unsigned,visible -string)

## Default Keys (Testing)
Usage/Client | Key change object | Key definition | Default value for testing
KEK (Key Encryption Key) | 0-0:43.0.0.255 Current Security setup | Master key (KEK) A unique key for each meter | 0x00 11 22 33 44 55 66 77 88 99 AA BB CC DD EE FF
Trust Anchor | 0-0:44.0.0.255 Image transfer | Root CA Certificate central certificate of the PKI | tbd
Sub CA | 0-0:43.0.0.255 Current Security setup | Sub CA Certificate 1 for DLMS Server certificates | tbd
|  | Sub CA Certificate 2 for DLMS Client certificates | tbd
DLMS - server | 0-0:43.0.0.255 Current Security setup | Server Certificate Server Digital Signature key certificate | tbd
Public client (WZ and LAN / WAN) | na | na | na
Management client (LAN/WAN) | 0-0:43.0.1.255 Security setup - Management Client | HES Certificate 1 Client Digital Signature key | tbd
|  | HES Certificate 2 Client Digital Signature key | tbd
|  | Global unicast encryption key A unique key for each meter | 0x00 01 02 03 04 05 06 07 08 09 0A 0B 0C 0D 0E 0F
|  | Global authentication key A unique key for each meter | 0xD0 D1 D2 D3 D4 D5 D6 D7 D8 D9 DA DB DC DD DE DF
Data Readout client (LAN/WAN) | 0-0:43.0.2.255 Security setup - Data Readout Client | HES Certificate 1 Client Digital Signature key | tbd
|  | HES Certificate 2 Client Digital Signature key | tbd
|  | Global unicast encryption key A unique key for each meter | 0x00 01 02 03 04 05 06 07 08 09 0A 0B 0C 0D 0E 0F
|  | Global authentication key A unique key for each meter | 0xD0 D1 D2 D3 D4 D5 D6 D7 D8 D9 DA DB DC DD DE DF
FW Update client (LAN) | na | na | na
PLC Management client (LAN) | 0-0:43.0.4.255 Security setup - Data Readout Client | HES Certificate 1 Client Digital Signature key | tbd
|  | HES Certificate 2 Client Digital Signature key | tbd
|  | Global unicast encryption key A unique key for each meter | 0x00 01 02 03 04 05 06 07 08 09 0A 0B 0C 0D 0E 0F
|  | Global authentication key A unique key for each meter | 0xD0 D1 D2 D3 D4 D5 D6 D7 D8 D9 DA DB DC DD DE DF
Installation client (WZ) | 0-0:40.0.5.255 Association LN - Installation Client | HLS secret A unique secret for each meter | 0x00 10 20 30 40 50 60 70 80 90 A0 B0 C0 D0 E0 F0 00 10 20 30 40 50 60 70 80 90 A0 B0 C0 D0 E0 F0
| 0-0:43.0.5.255 Security setup - Installation Client | Global unicast encryption key A unique key for each meter | 0x00 01 02 03 04 05 06 07 08 09 0A 0B 0C 0D 0E 0F
|  | Global authentication key A unique key for each meter | 0xD0 D1 D2 D3 D4 D5 D6 D7 D8 D9 DA DB DC DD DE DF
Maintenance client (WZ) | 0-0:40.0.6.255 Association LN - Maintenance Client | HLS secret A unique secret for each meter | 0x00 10 20 30 40 50 60 70 80 90 A0 B0 C0 D0 E0 F0 00 10 20 30 40 50 60 70 80 90 A0 B0 C0 D0 E0 F0
| 0-0:43.0.6.255 Security setup - Maintenance Client | Global unicast encryption key A unique key for each meter | 0x00 01 02 03 04 05 06 07 08 09 0A 0B 0C 0D 0E 0F
|  | Global authentication key A unique key for each meter | 0xD0 D1 D2 D3 D4 D5 D6 D7 D8 D9 DA DB DC DD DE DF
Certification client (WZ) | 0-0:40.0.7.255 Association LN - Certification Client | HLS secret A unique secret for each meter | 0x00 10 20 30 40 50 60 70 80 90 A0 B0 C0 D0 E0 F0 00 10 20 30 40 50 60 70 80 90 A0 B0 C0 D0 E0 F0
| 0-0:43.0.7.255 Security setup - Certification Client | Global unicast encryption key A unique key for each meter | 0x00 01 02 03 04 05 06 07 08 09 0A 0B 0C 0D 0E 0F
|  | Global authentication key A unique key for each meter | 0xD0 D1 D2 D3 D4 D5 D6 D7 D8 D9 DA DB DC DD DE DF
CIP - customer information client (H1) | 0-0:43.0.1.255 Security setup - Consumer Information | Global unicast encryption key A unique key for each meter | 0x10 11 12 13 14 15 16 17 18 19 1A 1B 1C 1D 1E 1F
G3 PLC Mac Layer | Key change object | Key definition | Default value for testing
KEK_PSK (Key Encryption Key) | 0-0:94.33.127.255 PLCG3_PSK_KEK | KEK for PSK A unique key for each meter | 0x00 11 22 33 44 55 66 77 88 99 AA BB CC DD EE FF
PSK | 0-0:94.33.128.255 PLCG3_PSK | PSK A unique key for each meter | 0x00 11 22 33 44 55 66 77 88 99 AA BB CC DD EE FF

## Push objects (hidden)
PUSH Objects
Objects concerning Push
# | Object / Attribute Name | Supported Objects |  | IC |  | Default Value
|  | 102 | 103 | Class | Ver.
| Push setup - Interval_1 | M | M | 40 | 0 | 0-1:25.9.0.255
| Push setup - Interval_2 | M | M | 40 | 0 | 0-2:25.9.0.255
| Push setup - Interval_3 | M | M | 40 | 0 | 0-3:25.9.0.255
| Push setup - On Power down | M | M | 40 | 0 | 0-5:25.9.0.255
| Push action scheduler - Interval_1 | M | M | 22 | 0 | 0-1:15.0.4.255
| Push action scheduler - Interval_2 | M | M | 22 | 0 | 0-2:15.0.4.255
| Push action scheduler - Interval_3 | M | M | 22 | 0 | 0-3:15.0.4.255
# | Object / Attribute Name | Supported Objects |  | IC |  | Default Value
|  | 102 | 103 | Class | Ver.
| Push setup - Customer Information | O | O | 40 | 0 | 0-6:25.9.0.255
| Push action scheduler - Customer Information | O | O | 22 | 0 | 0-4:15.0.4.255
| Security setup - Customer Information | O | O | 64 | 0 | 0-0:43.0.1.255
| IEC HDLC setup - Consumer Information port | O | O | 23 | 1 | 0-1:22.0.0.255
M=mandatory, O=optional, NA=not applicable